## LAB
LABORATORY
| OVERALL HEAT TRANSFER COEFFICIENT (U) | LENGTH | WIDTH | HEIGHT | EFFECTIVE AREA | LM | SHGF | SC | CLTD/TD @12 | CLTD (CORR) @12 | CLF @12 | COOLING LOAD q @12 | CLTD/TD @14 | CLTD (CORR) @14 | CLF @14 | COOLING LOAD q @14 | CLTD/TD @16 | CLTD (CORR) @16 | CLF @16 | COOLING LOAD q @16
ROOF | 1.09 | 8.077 | 5.03 |  | 40.6273 | 1 |  |  | 12 | 32.1 |  | 1421.5089 | 17 | 37.1 |  | 1642.9278 | 22 | 42.1 |  | 1864.3466
EXPOSED WALL (WEST) | 0.9059 | 8.077 |  | 3.65 | 29.481 | 0 |  |  | 5 | 24.1 |  | 643.6359 | 6.1111 | 25.21 |  | 673.2805 | 10 | 29.1 |  | 777.1703
FLOOR | 1.09 | 8.077 | 5.03 |  | 40.6273 |  |  |  | 18 |  |  | 797.1078 | 18 |  |  | 797.1078 | 18 |  |  | 797.1078
PARTITION WALL (EAST) | 1.349 | 8.077 |  | 3.65 | 24.0611 |  |  |  | 18 |  |  | 584.2504 | 18 |  |  | 584.2504 | 18 |  |  | 584.2504
PARTITION WALL (SOUTH) | 1.349 |  | 5.03 | 3.65 | 18.3595 |  |  |  | 18 |  |  | 445.8054 | 18 |  |  | 445.8054 | 18 |  |  | 445.8054
PARTITION WALL (NORTH)+DOOR | 1.5124 |  |  |  | 22.3215 |  |  |  | 18 |  |  | 607.6627 | 18 |  |  | 607.6627 | 18 |  |  | 499.8
2-GLASS WINDOWS (WEST) | 4.8 | 1.37 | 1.98 |  | 2.7126 |  | 670.311 | 0.6 | 18 |  | 0.17 | 839.6675 | 18 |  | 0.53 | 1625.1669 | 18 |  | 0.82 | 2257.9303
[10 empty] | TOTAL |  | 5339.6387 |  |  |  | 6376.2015 |  |  |  | 7226.4109
a=0.65 and b=C FROM Table-16 (OPERATIONAL HOURS 9 TO 19 (10 HRS))
| QUANTITY | INPUT | AREA | L.H.G | S.H.G. | CLF @12 | COOLING LOAD @12 | CLF @14 | COOLING LOAD @14 | CLF @16 | COOLING LOAD @16
LIGHTS | 5 | 2031.3655 | 40.6273 |  |  | 0.8 | 1625.0924 | 0.82 | 1665.7197 | 0.84 | 1706.347
PEOPLE (S.H.) | 10 |  |  |  | 73 | 0.77 | 562.1 | 0.83 | 605.9 | 0.87 | 635.1
PEOPLE (L.H.) | 10 |  |  | 59 |  |  | 590 |  | 590 |  | 590
HYSTEROSCOPIC PUMP (6 hrs) | 2 |  |  |  | 34 | 0.81 | 55.08 | 0.85 | 57.8 | 0.89 | 60.52
OPTICAL MICROSCOPE (6 hrs) | 5 |  |  |  | 63 | 0.81 | 255.15 | 0.85 | 267.75 | 0.89 | 280.35
LASER SONICS (6 hrs) | 3 |  |  |  | 229 | 0.81 | 556.47 | 0.85 | 583.95 | 0.89 | 611.43
ULTRASOUND SYSTEM (6 hrs) | 2 |  |  |  | 1050 | 0.81 | 1701 | 0.85 | 1785 | 0.89 | 1869
X-RAY SYSTEM (6 hrs) | 1 |  |  |  | 229 | 0.81 | 185.49 | 0.85 | 194.65 | 0.89 | 203.81
|  | TOTAL |  |  |  |  | 4940.3824 |  | 5160.7697 |  | 5366.557
| LENGTH | WIDTH | HEIGHT` | VOLUME | L/S | TD | HUMIDITY DIFFERENCE | COOLING LOAD
VENTILATION AND INFILTRATION (SENSIBLE) | 8.077 | 5.03 | 3.65 | 148.2897 | 82.3832 | 23 |  | 2334.4091
VENTILATION AND INFILTRATION (LATENT) | 8.077 | 5.03 | 3.65 | 148.2897 | 82.3832 |  | 0.0175 | 4342.4162
|  | q @12 hrs | q @14 hrs | q @16 hrs
| TOTAL SENSIBLE COOLOING LOAD | 12614.4302 | 13871.3804 | 14927.377
| TOTAL LATENT COOLOING LOAD | 4932.4162 | 4932.4162 | 4932.4162

## C-8
COUNSELOR OFFICE (C-8)
| OVERALL HEAT TRANSFER COEFFICIENT (U) | LENGTH | WIDTH | HEIGHT | EFFECTIVE AREA | LM | SHGF | SC | CLTD/TD @12 | CLTD (CORR) @12 | CLF @12 | COOLING LOAD q @12 | CLTD/TD @14 | CLTD (CORR) @14 | CLF @14 | COOLING LOAD q @14 | CLTD/TD @16 | CLTD (CORR) @16 | CLF @16 | COOLING LOAD q @16
ROOF | 1.09 | 8.077 | 5.03 |  | 40.6273 | 1 |  |  | 12 | 32.1 |  | 1421.5089 | 17 | 37.1 |  | 1642.9278 | 22 | 42.1 |  | 1864.3466
EXPOSED WALL (WEST) | 0.9059 | 8.077 |  | 3.65 | 29.481 | 0 |  |  | 5 | 24.1 |  | 643.6359 | 6.1111 | 25.21 |  | 673.2805 | 10 | 29.1 |  | 777.1703
FLOOR | 1.09 | 8.077 | 5.03 |  | 40.63 |  |  |  | 18 |  |  | 797.1606 | 18 |  |  | 797.1606 | 18 |  |  | 797.1606
PARTITION WALL (EAST) | 1.349 | 8.077 |  | 3.65 | 24.0611 |  |  |  | 18 |  |  | 584.2504 | 18 |  |  | 584.2504 | 18 |  |  | 584.2504
PARTITION WALL (NORTH)+DOOR | 1.5124 |  |  |  | 22.3215 |  |  |  | 18 |  |  | 607.6627 | 18 |  |  | 607.6627 | 18 |  |  | 499.8
2-GLASS WINDOWS (WEST) | 4.8 | 1.37 | 1.98 |  | 2.7126 |  | 670.311 | 0.6 | 18 |  | 0.17 | 839.6675 | 18 |  | 0.53 | 1625.1669 | 18 |  | 0.82 | 2257.9303
[10 empty] | TOTAL |  | 4893.8861 |  |  |  | 5930.4489 |  |  |  | 6780.6583
a=0.65 and b=C FROM Table-16
| QUANTITY | INPUT | AREA | L.H.G | S.H.G. | CLF @12 | COOLING LOAD @12 | CLF @14 | COOLING LOAD @14 | CLF @16 | COOLING LOAD @16
LIGHTS | 5 | 2031.3655 | 40.63 |  |  | 0.8 | 1625.0924 | 0.82 | 1665.7197 | 0.84 | 1706.347
PEOPLE (S.H.) | 6 |  |  |  | 72 | 0.77 | 332.64 | 0.83 | 358.56 | 0.87 | 375.84
PEOPLE (L.H.) | 6 |  |  | 45 |  |  | 270 |  | 270 |  | 270
COMPUTER | 4 |  |  |  | 65 | 0.81 | 210.6 | 0.85 | 221 | 0.89 | 231.4
PRINTER | 4 |  |  |  | 550 | 0.81 | 1782 | 0.85 | 1870 | 0.89 | 1958
|  | TOTAL |  |  |  |  | 3950.3324 |  | 4115.2797 |  | 4271.587
| LENGTH | WIDTH | HEIGHT` | VOLUME | L/S | TD | HUMIDITY DIFFERENCE | COOLING LOAD
VENTILATION AND INFILTRATION (SENSIBLE) | 8.077 | 5.03 | 3.65 | 148.2897 | 82.3832 | 23 |  | 2334.4091
VENTILATION AND INFILTRATION (LATENT) | 8.077 | 5.03 | 3.65 | 148.2897 | 82.3832 |  | 0.0175 | 4342.4162
|  | q @12 hrs | q @14 hrs | q @16 hrs
| TOTAL SENSIBLE COOLOING LOAD | 11178.6276 | 12380.1378 | 13386.6544
| TOTAL LATENT COOLOING LOAD | 4612.4162 | 4612.4162 | 4612.4162

## P-2+STORE
PHLEBOTOMY + STORAGE
| OVERALL HEAT TRANSFER COEFFICIENT (U) | LENGTH | WIDTH | HEIGHT | EFFECTIVE AREA | LM | SHGF | SC | CLTD/TD @12 | CLTD (CORR) @12 | CLF @12 | COOLING LOAD q @12 | CLTD/TD @14 | CLTD (CORR) @14 | CLF @14 | COOLING LOAD q @14 | CLTD/TD @16 | CLTD (CORR) @16 | CLF @16 | COOLING LOAD q @16
ROOF | 1.09 | 8.077 | 5.03 |  | 40.6273 | 1 |  |  | 12 | 32.1 |  | 1421.5089 | 17 | 37.1 |  | 1642.9278 | 22 | 42.1 |  | 1864.3466
FLOOR | 1.09 | 8.077 | 5.03 |  | 40.63 |  |  |  | 18 |  |  | 797.1606 | 18 |  |  | 797.1606 | 18 |  |  | 797.1606
PARTITION WALL (WEST) | 1.349 | 8.077 |  | 3.65 | 24.0611 |  |  |  | 18 |  |  | 584.2504 | 18 |  |  | 584.2504 | 18 |  |  | 584.2504
PARTITION WALL (EAST)+DOOR | 1.5124 |  |  |  | 33.443 |  |  |  | 18 |  |  | 910.4268 | 18 |  |  | 910.4268 | 18 |  |  | 499.8
PARTITION WALL (NORTH) | 1.349 |  | 5.03 | 3.65 | 18.3595 |  |  |  | 18 |  |  | 445.8054 | 18 |  |  | 445.8054 | 18 |  |  | 445.8054
PARTITION WALL (SOUTH) | 1.349 |  | 5.03 | 3.65 | 18.3595 |  |  |  | 18 |  |  | 445.8054 | 18 |  |  | 445.8054 | 18 |  |  | 445.8054
2-GLASS WINDOWS (WEST) | 4.8 | 1.37 | 1.98 |  | 2.7126 |  | 670.311 | 0.6 | 18 |  | 0.17 | 839.6675 | 18 |  | 0.53 | 1625.1669 | 18 |  | 0.82 | 2257.9303
[10 empty] | TOTAL |  | 5444.6251 |  |  |  | 6451.5433 |  |  |  | 6895.0987
7.01
a=0.65 and b=C FROM Table-16
| QUANTITY | INPUT | AREA | L.H.G | S.H.G. | CLF @12 | COOLING LOAD @12 | CLF @14 | COOLING LOAD @14 | CLF @16 | COOLING LOAD @16
LIGHTS | 8 | 3250.1848 | 40.63 |  |  | 0.8 | 2600.1478 | 0.82 | 2665.1515 | 0.84 | 2730.1552
PEOPLE (S.H.) | 10 |  |  |  | 72 | 0.77 | 554.4 | 0.83 | 597.6 | 0.87 | 626.4
PEOPLE (L.H.) | 10 |  |  | 45 |  |  | 450 |  | 450 |  | 450
COMPUTER | 4 |  |  |  | 65 | 0.81 | 210.6 | 0.85 | 221 | 0.89 | 231.4
PRINTER | 4 |  |  |  | 550 | 0.81 | 1782 | 0.85 | 1870 | 0.89 | 1958
|  | TOTAL |  |  |  |  | 5147.1478 |  | 5353.7515 |  | 5545.9552
| LENGTH | WIDTH | HEIGHT` | VOLUME | L/S | TD | HUMIDITY DIFFERENCE | COOLING LOAD
VENTILATION AND INFILTRATION (SENSIBLE) | 8.077 | 5.03 | 3.65 | 148.2897 | 82.3832 | 23 |  | 2334.4091
VENTILATION AND INFILTRATION (LATENT) | 8.077 | 5.03 | 3.65 | 148.2897 | 82.3832 |  | 0.0175 | 4342.4162
|  | q @12 hrs | q @14 hrs | q @16 hrs
| TOTAL SENSIBLE COOLOING LOAD | 12926.1821 | 14139.704 | 14775.4631
| TOTAL LATENT COOLOING LOAD | 4792.4162 | 4792.4162 | 4792.4162

## P-1
PHLEBOTOMY-2
| OVERALL HEAT TRANSFER COEFFICIENT (U) | LENGTH | WIDTH | HEIGHT | EFFECTIVE AREA | LM | SHGF | SC | CLTD/TD @12 | CLTD (CORR) @12 | CLF @12 | COOLING LOAD q @12 | CLTD/TD @14 | CLTD (CORR) @14 | CLF @14 | COOLING LOAD q @14 | CLTD/TD @16 | CLTD (CORR) @16 | CLF @16 | COOLING LOAD q @16
ROOF | 1.09 | 5.03 | 10.06 |  | 50.6018 | 1 |  |  | 12 | 32.1 |  | 1770.5064 | 17 | 37.1 |  | 2046.2862 | 22 | 42.1 |  | 2322.066
EXPOSED WALL (WEST) | 0.9059 | 5.03 |  | 3.65 | 18.3595 | 0 |  |  | 5 | 24.1 |  | 400.8281 | 6.1111 | 25.21 |  | 419.2895 | 10 | 29.1 |  | 483.9874
FLOOR | 1.09 | 5.03 | 10.06 |  | 50.6018 |  |  |  | 18 |  |  | 992.8073 | 18 |  |  | 992.8073 | 18 |  |  | 992.8073
PARTITION WALL (NORTH) | 1.349 | 5.03 |  | 3.65 | 18.3595 |  |  |  | 18 |  |  | 445.8054 | 18 |  |  | 445.8054 | 18 |  |  | 445.8054
PARTITION WALL (EAST)+DOOR | 1.5124 |  |  |  | 22.3215 |  |  |  | 18 |  |  | 607.6627 | 18 |  |  | 607.6627 | 18 |  |  | 499.8
GLASS WINDOWS (WEST) | 4.8 | 1.37 | 1.98 |  | 2.7126 |  | 670.311 | 0.6 | 18 |  | 0.17 | 419.8338 | 18 |  | 0.53 | 812.5835 | 18 |  | 0.82 | 1128.9652
[10 empty] | TOTAL |  | 4637.4436 |  |  |  | 5324.4345 |  |  |  | 5873.4313
a=0.65 and b=C FROM Table-16 (OPERATIONAL HOURS 9 TO 19 (10 HRS))
| QUANTITY | INPUT | AREA | L.H.G | S.H.G. | CLF @12 | COOLING LOAD @12 | CLF @14 | COOLING LOAD @14 | CLF @16 | COOLING LOAD @16
LIGHTS | 8 | 4048.144 | 50.6018 |  |  | 0.8 | 3238.5152 | 0.82 | 3319.4781 | 0.84 | 3400.441
PEOPLE (S.H.) | 10 |  |  |  | 73 | 0.77 | 562.1 | 0.83 | 605.9 | 0.87 | 635.1
PEOPLE (L.H.) | 10 |  |  | 59 |  |  | 590 |  | 590 |  | 590
COMPUTER | 4 |  |  |  | 65 | 0.81 | 210.6 | 0.85 | 221 | 0.89 | 231.4
|  | TOTAL |  |  |  |  | 4011.2152 |  | 4146.3781 |  | 4266.941
| LENGTH | WIDTH | HEIGHT` | VOLUME | L/S | TD | HUMIDITY DIFFERENCE | COOLING LOAD
VENTILATION AND INFILTRATION (SENSIBLE) | 5.03 | 10.06 | 3.65 | 184.6966 | 102.6092 | 23 |  | 2907.5344
VENTILATION AND INFILTRATION (LATENT) | 5.03 | 10.06 | 3.65 | 184.6966 | 102.6092 |  | 0.0175 | 5408.5312
|  | q @12 hrs | q @14 hrs | q @16 hrs
| TOTAL SENSIBLE COOLOING LOAD | 11556.1932 | 12378.347 | 13047.9067
| TOTAL LATENT COOLOING LOAD | 5998.5312 | 5998.5312 | 5998.5312

## ROUTINE CHECK UP ROOM
ROUTINE CHECK UP ROOM
| OVERALL HEAT TRANSFER COEFFICIENT (U) | LENGTH | WIDTH | HEIGHT | EFFECTIVE AREA | LM | SHGF | SC | CLTD/TD @12 | CLTD (CORR) @12 | CLF @12 | COOLING LOAD q @12 | CLTD/TD @14 | CLTD (CORR) @14 | CLF @14 | COOLING LOAD q @14 | CLTD/TD @16 | CLTD (CORR) @16 | CLF @16 | COOLING LOAD q @16
ROOF | 1.09 | 8.077 | 5.03 |  | 40.6273 | 1 |  |  | 12 | 32.1 |  | 1421.5089 | 17 | 37.1 |  | 1642.9278 | 22 | 42.1 |  | 1864.3466
EXPOSED WALL (EAST) | 0.9059 | 8.077 |  | 3.65 | 29.481 | -3 |  |  | 15 | 31.1 |  | 830.5841 | 17.7778 | 33.8778 |  | 904.7699 | 18.3333 | 34.4333 |  | 919.607
FLOOR | 1.09 | 8.077 | 5.03 |  | 40.6273 |  |  |  | 18 |  |  | 797.1078 | 18 |  |  | 797.1078 | 18 |  |  | 797.1078
PARTITION WALL (WEST) | 1.349 | 8.077 |  | 3.65 | 29.481 |  |  |  | 18 |  |  | 715.8589 | 18 |  |  | 715.8589 | 18 |  |  | 715.8589
PARTITION WALL (NORTH)+DOOR | 1.5124 |  |  |  | 22.3215 |  |  |  | 18 |  |  | 607.6627 | 18 |  |  | 607.6627 | 18 |  |  | 499.8
2-GLASS WINDOWS (EAST) | 4.8 | 1.37 | 1.98 |  | 2.7126 |  | 670.311 | 0.6 | 18 |  | 0.27 | 1057.8618 | 18 |  | 0.22 | 948.7647 | 18 |  | 0.17 | 839.6675
[10 empty] | TOTAL |  | 5430.5842 |  |  |  | 5617.0917 |  |  |  | 5636.3879
a=0.65 and b=C FROM Table-16 (OPERATIONAL HOURS 9 TO 21 (12 HRS))
| QUANTITY | INPUT | AREA | L.H.G | S.H.G. | CLF @12 | COOLING LOAD @12 | CLF @14 | COOLING LOAD @14 | CLF @16 | COOLING LOAD @16
LIGHTS | 8 | 3250.1848 | 40.63 |  |  | 0.81 | 2632.6497 | 0.84 | 2730.1552 | 0.86 | 2795.1589
PEOPLE (S.H.) | 8 |  |  |  | 73 | 0.79 | 461.36 | 0.84 | 490.56 | 0.88 | 513.92
PEOPLE (L.H.) | 8 |  |  | 59 |  |  | 472 |  | 472 |  | 472
COMPUTER | 4 |  |  |  | 65 | 0.82 | 213.2 | 0.86 | 223.6 | 0.89 | 231.4
PRINTER | 4 |  |  |  | 550 | 0.82 | 1804 | 0.86 | 1892 | 0.89 | 1958
PULSE OXIMETER | 3 |  |  |  | 20 | 0.69 | 41.4 | 0.77 | 46.2 | 0.82 | 49.2
|  | TOTAL |  |  |  |  | 5152.6097 |  | 5382.5152 |  | 5547.6789
| LENGTH | WIDTH | HEIGHT` | VOLUME | L/S | TD | HUMIDITY DIFFERENCE | COOLING LOAD
VENTILATION AND INFILTRATION (SENSIBLE) | 8.077 | 5.03 | 3.65 | 148.2897 | 82.3832 | 23 |  | 2334.4091
VENTILATION AND INFILTRATION (LATENT) | 8.077 | 5.03 | 3.65 | 148.2897 | 82.3832 |  | 0.0175 | 4342.4162
|  | q @12 hrs | q @14 hrs | q @16 hrs
| TOTAL SENSIBLE COOLOING LOAD | 12917.603 | 13334.016 | 13518.4759
| TOTAL LATENT COOLOING LOAD | 4814.4162 | 4814.4162 | 4814.4162

## HELP DESK
HELP DESK
| OVERALL HEAT TRANSFER COEFFICIENT (U) | LENGTH | WIDTH | HEIGHT | EFFECTIVE AREA | LM | SHGF | SC | CLTD/TD @12 | CLTD (CORR) @12 | CLF @12 | COOLING LOAD q @12 | CLTD/TD @14 | CLTD (CORR) @14 | CLF @14 | COOLING LOAD q @14 | CLTD/TD @16 | CLTD (CORR) @16 | CLF @16 | COOLING LOAD q @16
ROOF | 1.09 | 3.23 | 5.03 |  | 16.2469 | 1 |  |  | 12 | 32.1 |  | 568.4628 | 17 | 37.1 |  | 657.0084 | 22 | 42.1 |  | 745.554
FLOOR | 1.09 | 3.23 | 5.03 |  | 40.63 |  |  |  | 18 |  |  | 797.1606 | 18 |  |  | 797.1606 | 18 |  |  | 797.1606
PARTITION WALL (WEST) | 1.349 | 3.23 |  | 3.65 | 11.7895 |  |  |  | 18 |  |  | 286.2726 | 18 |  |  | 286.2726 | 18 |  |  | 286.2726
PARTITION WALL (EAST)+DOOR | 1.5124 |  |  |  | 15.7515 |  |  |  | 18 |  |  | 428.8062 | 18 |  |  | 428.8062 | 18 |  |  | 499.8
PARTITION WALL (SOUTH) | 1.349 | 3.23 |  | 3.65 | 11.7895 |  |  |  | 18 |  |  | 286.2726 | 18 |  |  | 286.2726 | 18 |  |  | 499.8
PARTITION WALL (NORTH ) | 1.7935 |  |  |  | 21.07 |  |  |  | 18 |  |  | 680.2028 | 18 |  |  | 680.2028 | 18 |  |  | 499.8
GLASS WINDOWS (NORTH) | 4.8 | 1.37 | 1.98 |  | 2.7126 |  | 141.615 | 0.6 | 18 |  | 0.89 | 439.502 | 18 |  | 0.86 | 432.5874 | 18 |  | 0.75 | 407.2338
[10 empty] | TOTAL |  | 3486.6797 |  |  |  | 3568.3107 |  |  |  | 3735.6211
a=0.65 and b=C FROM Table-16 (OPERATIONAL HOURS 7 TO 11 (16 HRS))
| QUANTITY | INPUT | AREA | L.H.G | S.H.G. | CLF @12 | COOLING LOAD @12 | CLF @14 | COOLING LOAD @14 | CLF @16 | COOLING LOAD @16
LIGHTS | 2 | 324.938 | 16.2469 |  |  | 0.86 | 279.4467 | 0.88 | 285.9454 | 0.89 | 289.1948
PEOPLE (S.H.) | 3 |  |  |  | 72 | 0.82 | 177.12 | 0.87 | 187.92 | 0.9 | 194.4
PEOPLE (L.H.) | 3 |  |  | 45 |  |  | 135 |  | 135 |  | 135
COMPUTER | 3 |  |  |  | 65 | 0.85 | 165.75 | 0.89 | 173.55 | 0.91 | 177.45
PRINTER | 3 |  |  |  | 550 | 0.85 | 1402.5 | 0.89 | 1468.5 | 0.91 | 1501.5
|  | TOTAL |  |  |  |  | 2024.8167 |  | 2115.9154 |  | 2162.5448
| LENGTH | WIDTH | HEIGHT` | VOLUME | L/S | TD | HUMIDITY DIFFERENCE | COOLING LOAD
VENTILATION AND INFILTRATION (SENSIBLE) | 3.23 | 5.03 | 3.65 | 59.3012 | 32.9451 | 23 |  | 933.5324
VENTILATION AND INFILTRATION (LATENT) | 3.23 | 5.03 | 3.65 | 59.3012 | 32.9451 |  | 0.0175 | 1736.5364
|  | q @12 hrs | q @14 hrs | q @16 hrs
| TOTAL SENSIBLE COOLOING LOAD | 6445.0288 | 6617.7586 | 6831.6983
| TOTAL LATENT COOLOING LOAD | 1871.5364 | 1871.5364 | 1871.5364

## STORE-2
STORE-2
| OVERALL HEAT TRANSFER COEFFICIENT (U) | LENGTH | WIDTH | HEIGHT | EFFECTIVE AREA | LM | SHGF | SC | CLTD/TD @12 | CLTD (CORR) @12 | CLF @12 | COOLING LOAD q @12 | CLTD/TD @14 | CLTD (CORR) @14 | CLF @14 | COOLING LOAD q @14 | CLTD/TD @16 | CLTD (CORR) @16 | CLF @16 | COOLING LOAD q @16
ROOF | 1.09 | 4.039 | 5.03 |  | 20.3162 | 1 |  |  | 12 | 32.1 |  | 710.8425 | 17 | 37.1 |  | 821.5656 | 22 | 42.1 |  | 932.2887
FLOOR | 1.09 | 4.039 | 5.03 |  | 40.63 |  |  |  | 18 |  |  | 797.1606 | 18 |  |  | 797.1606 | 18 |  |  | 797.1606
PARTITION WALL (WEST) | 1.349 | 4.039 |  | 3.65 | 14.7423 |  |  |  | 18 |  |  | 357.9737 | 18 |  |  | 357.9737 | 18 |  |  | 357.9737
PARTITION WALL (EAST)+DOOR | 1.5124 |  |  |  | 15.7515 |  |  |  | 18 |  |  | 428.8062 | 18 |  |  | 428.8062 | 18 |  |  | 499.8
PARTITION WALL (NORTH) | 1.349 | 3.23 |  | 3.65 | 11.7895 |  |  |  | 18 |  |  | 286.2726 | 18 |  |  | 286.2726 | 18 |  |  | 499.8
PARTITION WALL (SOUTH ) | 1.7935 |  |  |  | 21.07 |  |  |  | 18 |  |  | 680.2028 | 18 |  |  | 680.2028 | 18 |  |  | 499.8
GLASS WINDOWS (SOUTH) | 4.8 | 1.37 | 1.98 |  | 2.7126 |  | 144.762 | 0.6 | 18 |  | 0.83 | 429.924 | 18 |  | 0.68 | 394.5827 | 18 |  | 0.35 | 316.8317
[11 empty] | TOTAL | 3691.1825 |  |  |  | 3766.5643 |  |  |  | 3903.6548
a=0.65 and b=C FROM Table-16 (OPERATIONAL HOURS 9 TO 19 (10 HRS))
| QUANTITY | INPUT | AREA | L.H.G | S.H.G. | CLF @12 | COOLING LOAD @12 | CLF @14 | COOLING LOAD @14 | CLF @16 | COOLING LOAD @16
LIGHTS | 2 | 406.3234 | 20.3162 |  |  | 0.8 | 325.0587 | 0.82 | 333.1852 | 0.84 | 341.3117
PEOPLE (S.H.) | 1 |  |  |  | 72 | 0.77 | 55.44 | 0.83 | 59.76 | 0.87 | 62.64
PEOPLE (L.H.) | 1 |  |  | 45 |  |  | 45 |  | 45 |  | 45
COMPUTER | 3 |  |  |  | 65 | 0.81 | 157.95 | 0.85 | 165.75 | 0.89 | 173.55
|  | TOTAL |  |  |  |  | 538.4487 |  | 558.6952 |  | 577.5017
| LENGTH | WIDTH | HEIGHT` | VOLUME | L/S | TD | HUMIDITY DIFFERENCE | COOLING LOAD
VENTILATION AND INFILTRATION (SENSIBLE) | 4.039 | 5.03 | 3.65 | 74.154 | 41.1967 | 23 |  | 1167.3491
VENTILATION AND INFILTRATION (LATENT) | 4.039 | 5.03 | 3.65 | 74.154 | 41.1967 |  | 0.0175 | 2171.4769
|  | q @12 hrs | q @14 hrs | q @16 hrs
| TOTAL SENSIBLE COOLOING LOAD | 5396.9803 | 5492.6085 | 5648.5055
| TOTAL LATENT COOLOING LOAD | 2216.4769 | 2216.4769 | 2216.4769

## FEMALE TOILET
FEMALE TOILET
| OVERALL HEAT TRANSFER COEFFICIENT (U) | LENGTH | WIDTH | HEIGHT | EFFECTIVE AREA | LM | SHGF | SC | CLTD/TD @12 | CLTD (CORR) @12 | CLF @12 | COOLING LOAD q @12 | CLTD/TD @14 | CLTD (CORR) @14 | CLF @14 | COOLING LOAD q @14 | CLTD/TD @16 | CLTD (CORR) @16 | CLF @16 | COOLING LOAD q @16
ROOF | 1.09 | 4.04 | 3.96 |  | 15.9984 | 1 |  |  | 12 | 32.1 |  | 559.768 | 17 | 37.1 |  | 646.9593 | 22 | 42.1 |  | 734.1506
FLOOR | 1.09 | 4.04 | 3.96 |  | 15.9984 |  |  |  | 18 |  |  | 313.8886 | 18 |  |  | 313.8886 | 18 |  |  | 313.8886
PARTITION WALL (SOUTH) | 1.349 |  | 3.96 | 3.65 | 14.454 |  |  |  | 18 |  |  | 350.972 | 18 |  |  | 350.972 | 18 |  |  | 350.972
PARTITION WALL (NORTH)+DOOR | 1.5467 |  |  |  | 18.42 |  |  |  | 18 |  |  | 512.8239 | 18 |  |  | 512.8239 | 18 |  |  | 499.8
PARTITION WALL (WEST) | 1.4339 |  |  |  | 1.4339 |  |  |  | 18 |  |  | 37.0092 | 18 |  |  | 37.0092 | 18 |  |  | 499.8
PARTITION WALL (EAST) | 1.349 | 4.04 |  | 3.65 | 14.746 |  |  |  | 18 |  |  | 358.0624 | 18 |  |  | 358.0624 | 18 |  |  | 499.8
GLASS WINDOWS (WEST) | 4.8 | 0.61 | 0.61 |  | 0.3721 |  | 670.311 | 0.6 | 18 |  | 0.17 | 57.5906 | 18 |  | 0.53 | 111.4659 | 18 |  | 0.82 | 154.8654
[10 empty] | TOTAL |  | 2190.1147 |  |  |  | 2331.1813 |  |  |  | 3053.2766
a=0.65 and b=C FROM Table-16
| QUANTITY | INPUT | AREA | L.H.G | S.H.G. | CLF @12 | COOLING LOAD @12 | CLF @14 | COOLING LOAD @14 | CLF @16 | COOLING LOAD @16
LIGHTS | 2 | 319.968 | 15.9984 |  |  | 0.86 | 275.1725 | 0.88 | 281.5718 | 0.89 | 284.7715
PEOPLE (S.H.) | 3 |  |  |  | 73 | 0.82 | 179.58 | 0.87 | 190.53 | 0.9 | 197.1
PEOPLE (L.H.) | 3 |  |  | 59 |  |  | 177 |  | 177 |  | 177
|  | TOTAL |  |  |  |  | 454.7525 |  | 454.7525 |  | 481.8715
| LENGTH | WIDTH | HEIGHT` | VOLUME | L/S | TD | HUMIDITY DIFFERENCE | COOLING LOAD
VENTILATION AND INFILTRATION (SENSIBLE) | 4.04 | 3.96 | 3.65 | 58.3942 | 32.4412 | 23 |  | 919.2538
VENTILATION AND INFILTRATION (LATENT) | 4.04 | 3.96 | 3.65 | 58.3942 | 32.4412 |  | 0.0175 | 1709.9757
|  | q @12 hrs | q @14 hrs | q @16 hrs
| TOTAL SENSIBLE COOLOING LOAD | 3564.121 | 3705.1876 | 4454.402
| TOTAL LATENT COOLOING LOAD | 1886.9757 | 1886.9757 | 1886.9757

## MALE TOILET
MALE TOILET
| OVERALL HEAT TRANSFER COEFFICIENT (U) | LENGTH | WIDTH | HEIGHT | EFFECTIVE AREA | LM | SHGF | SC | CLTD/TD @12 | CLTD (CORR) @12 | CLF @12 | COOLING LOAD q @12 | CLTD/TD @14 | CLTD (CORR) @14 | CLF @14 | COOLING LOAD q @14 | CLTD/TD @16 | CLTD (CORR) @16 | CLF @16 | COOLING LOAD q @16
ROOF | 1.09 | 4.04 | 3.96 |  | 15.9984 | 1 |  |  | 12 | 32.1 |  | 559.768 | 17 | 37.1 |  | 646.9593 | 22 | 42.1 |  | 734.1506
FLOOR | 1.09 | 4.04 | 3.96 |  | 15.9984 |  |  |  | 18 |  |  | 313.8886 | 18 |  |  | 313.8886 | 18 |  |  | 313.8886
PARTITION WALL (NORTH) | 1.349 |  | 3.96 | 3.65 | 14.454 |  |  |  | 18 |  |  | 350.972 | 18 |  |  | 350.972 | 18 |  |  | 350.972
PARTITION WALL (SOUTH)+DOOR | 1.5467 |  |  |  | 18.42 |  |  |  | 18 |  |  | 512.8239 | 18 |  |  | 512.8239 | 18 |  |  | 499.8
PARTITION WALL (WEST) | 1.4339 |  |  |  | 1.4339 |  |  |  | 18 |  |  | 37.0092 | 18 |  |  | 37.0092 | 18 |  |  | 499.8
PARTITION WALL (EAST) | 1.349 | 4.04 |  | 3.65 | 14.746 |  |  |  | 18 |  |  | 358.0624 | 18 |  |  | 358.0624 | 18 |  |  | 499.8
GLASS WINDOWS (WEST) | 4.8 | 0.61 | 0.61 |  | 0.3721 |  | 670.311 | 0.6 | 18 |  | 0.17 | 57.5906 | 18 |  | 0.53 | 111.4659 | 18 |  | 0.82 | 154.8654
[10 empty] | TOTAL |  | 2190.1147 |  |  |  | 2331.1813 |  |  |  | 3053.2766
a=0.65 and b=C FROM Table-16
| QUANTITY | INPUT | AREA | L.H.G | S.H.G. | CLF @12 | COOLING LOAD @12 | CLF @14 | COOLING LOAD @14 | CLF @16 | COOLING LOAD @16
LIGHTS | 2 | 319.968 | 15.9984 |  |  | 0.86 | 275.1725 | 0.88 | 281.5718 | 0.89 | 284.7715
PEOPLE (S.H.) | 3 |  |  |  | 73 | 0.82 | 179.58 | 0.87 | 190.53 | 0.9 | 197.1
PEOPLE (L.H.) | 3 |  |  | 59 |  |  | 177 |  | 177 |  | 177
|  | TOTAL |  |  |  |  | 454.7525 |  | 472.1018 |  | 481.8715
| LENGTH | WIDTH | HEIGHT` | VOLUME | L/S | TD | HUMIDITY DIFFERENCE | COOLING LOAD
VENTILATION AND INFILTRATION (SENSIBLE) | 4.04 | 3.96 | 3.65 | 58.3942 | 32.4412 | 23 |  | 919.2538
VENTILATION AND INFILTRATION (LATENT) | 4.04 | 3.96 | 3.65 | 58.3942 | 32.4412 |  | 0.0175 | 1709.9757
|  | q @12 hrs | q @14 hrs | q @16 hrs
| TOTAL SENSIBLE COOLOING LOAD | 3564.121 | 3722.537 | 4454.402
| TOTAL LATENT COOLOING LOAD | 1886.9757 | 1886.9757 | 1886.9757

## MEDICAL STORE-1
MEDICAL STORE-1
| OVERALL HEAT TRANSFER COEFFICIENT (U) | LENGTH | WIDTH | HEIGHT | EFFECTIVE AREA | LM | SHGF | SC | CLTD/TD @12 | CLTD (CORR) @12 | CLF @12 | COOLING LOAD q @12 | CLTD/TD @14 | CLTD (CORR) @14 | CLF @14 | COOLING LOAD q @14 | CLTD/TD @16 | CLTD (CORR) @16 | CLF @16 | COOLING LOAD q @16
ROOF | 1.09 | 4.04 | 3.96 |  | 15.9984 | 1 |  |  | 12 | 32.1 |  | 559.768 | 17 | 37.1 |  | 646.9593 | 22 | 42.1 |  | 734.1506
FLOOR | 1.09 | 4.04 | 3.96 |  | 15.9984 |  |  |  | 18 |  |  | 313.8886 | 18 |  |  | 313.8886 | 18 |  |  | 313.8886
PARTITION WALL (EAST) | 1.349 | 4.04 |  | 3.65 | 14.746 |  |  |  | 18 |  |  | 358.0624 | 18 |  |  | 358.0624 | 18 |  |  | 358.0624
PARTITION WALL (NORTH)+DOOR | 1.5467 |  |  |  | 18.42 |  |  |  | 18 |  |  | 512.8239 | 18 |  |  | 512.8239 | 18 |  |  | 499.8
PARTITION WALL (WEST) | 1.4339 |  |  |  | 1.4339 |  |  |  | 18 |  |  | 37.0092 | 18 |  |  | 37.0092 | 18 |  |  | 499.8
PARTITION WALL (SOUTH) | 1.5676 | 4.04 |  | 3.65 | 15.75 |  |  |  | 18 |  |  | 444.4146 | 18 |  |  | 444.4146 | 18 |  |  | 499.8
GLASS WINDOWS (WEST) | 4.8 | 1 | 1 |  | 1 |  | 670.311 | 0.6 | 18 |  | 0.17 | 154.7717 | 18 |  | 0.53 | 299.5589 | 18 |  | 0.82 | 416.193
[10 empty] | TOTAL |  | 2380.7384 |  |  |  | 2612.7169 |  |  |  | 3321.6946
a=0.65 and b=C FROM Table-16
| QUANTITY | INPUT | AREA | L.H.G | S.H.G. | CLF @12 | COOLING LOAD @12 | CLF @14 | COOLING LOAD @14 | CLF @16 | COOLING LOAD @16
LIGHTS | 2 | 319.968 | 15.9984 |  |  | 0.86 | 275.1725 | 0.88 | 281.5718 | 0.89 | 284.7715
PEOPLE (S.H.) | 5 |  |  |  | 73 | 0.82 | 299.3 | 0.87 | 317.55 | 0.9 | 328.5
PEOPLE (L.H.) | 5 |  |  | 59 |  |  | 295 |  | 295 |  | 295
COMPUTER | 3 |  |  |  | 65 | 0.85 | 165.75 | 0.89 | 173.55 | 0.91 | 177.45
PRINTER | 3 |  |  |  | 550 | 0.85 | 1402.5 | 0.89 | 1468.5 | 0.91 | 1501.5
|  | TOTAL |  |  |  |  | 2142.7225 |  | 2241.1718 |  | 2292.2215
| LENGTH | WIDTH | HEIGHT` | VOLUME | L/S | TD | HUMIDITY DIFFERENCE | COOLING LOAD
VENTILATION AND INFILTRATION (SENSIBLE) | 4.04 | 3.96 | 3.65 | 58.3942 | 32.4412 | 23 |  | 919.2538
VENTILATION AND INFILTRATION (LATENT) | 4.04 | 3.96 | 3.65 | 58.3942 | 32.4412 |  | 0.0175 | 1709.9757
|  | q @12 hrs | q @14 hrs | q @16 hrs
| TOTAL SENSIBLE COOLOING LOAD | 5442.7147 | 5773.1426 | 6533.1699
| TOTAL LATENT COOLOING LOAD | 2004.9757 | 2004.9757 | 2004.9757

## STAFF ROOM
STAFF ROOM
| OVERALL HEAT TRANSFER COEFFICIENT (U) | LENGTH | WIDTH | HEIGHT | EFFECTIVE AREA | LM | SHGF | SC | CLTD/TD @12 | CLTD (CORR) @12 | CLF @12 | COOLING LOAD q @12 | CLTD/TD @14 | CLTD (CORR) @14 | CLF @14 | COOLING LOAD q @14 | CLTD/TD @16 | CLTD (CORR) @16 | CLF @16 | COOLING LOAD q @16
ROOF | 1.09 | 4.04 | 3.96 |  | 15.9984 | 1 |  |  | 12 | 32.1 |  | 559.768 | 17 | 37.1 |  | 646.9593 | 22 | 42.1 |  | 734.1506
FLOOR | 1.09 | 4.04 | 3.96 |  | 15.9984 |  |  |  | 18 |  |  | 313.8886 | 18 |  |  | 313.8886 | 18 |  |  | 313.8886
PARTITION WALL (NORTH) | 1.349 |  | 3.96 | 3.65 | 14.454 |  |  |  | 18 |  |  | 350.972 | 18 |  |  | 350.972 | 18 |  |  | 350.972
PARTITION WALL (SOUTH)+DOOR | 1.5467 |  |  |  | 18.42 |  |  |  | 18 |  |  | 512.8239 | 18 |  |  | 512.8239 | 18 |  |  | 499.8
PARTITION WALL (EAST) | 1.349 | 4.04 |  | 3.65 | 14.746 |  |  |  | 18 |  |  | 358.0624 | 18 |  |  | 358.0624 | 18 |  |  | 499.8
PARTITION WALL (WEST) | 1.5676 | 4.04 |  | 3.65 | 15.75 |  |  |  | 18 |  |  | 444.4146 | 18 |  |  | 444.4146 | 18 |  |  | 499.8
GLASS WINDOWS (WEST) | 4.8 | 1 | 1 |  | 1 |  | 670.311 | 0.6 | 18 |  | 0.17 | 154.7717 | 18 |  | 0.53 | 299.5589 | 18 |  | 0.82 | 416.193
[10 empty] | TOTAL |  | 2694.7012 |  |  |  | 2926.6797 |  |  |  | 3314.6042
a=0.65 and b=C FROM Table-16
| QUANTITY | INPUT | AREA | L.H.G | S.H.G. | CLF @12 | COOLING LOAD @12 | CLF @14 | COOLING LOAD @14 | CLF @16 | COOLING LOAD @16
LIGHTS | 2 | 319.968 | 15.9984 |  |  | 0.8 | 255.9744 | 0.82 | 262.3738 | 0.84 | 268.7731
PEOPLE (S.H.) | 5 |  |  |  | 73 | 0.74 | 270.1 | 0.8 | 292 | 0.85 | 310.25
PEOPLE (L.H.) | 5 |  |  | 59 |  |  | 295 |  | 295 |  | 295
COMPUTER | 3 |  |  |  | 65 | 0.81 | 157.95 | 0.85 | 165.75 | 0.89 | 173.55
PRINTER | 3 |  |  |  | 550 | 0.81 | 1336.5 | 0.85 | 1402.5 | 0.89 | 1468.5
COFFEE BREWER | 1 |  |  | 560 | 1100 | 0.81 | 1451 | 0.85 | 1495 | 0.89 | 1539
|  | TOTAL |  |  |  |  | 3471.5244 |  | 3617.6238 |  | 3760.0731
CONSIDER LATENT HEAT FOR THE COFFE BREWER
| LENGTH | WIDTH | HEIGHT` | VOLUME | L/S | TD | HUMIDITY DIFFERENCE | COOLING LOAD
VENTILATION AND INFILTRATION (SENSIBLE) | 4.04 | 3.96 | 3.65 | 58.3942 | 32.4412 | 23 |  | 919.2538
VENTILATION AND INFILTRATION (LATENT) | 4.04 | 3.96 | 3.65 | 58.3942 | 32.4412 |  | 0.0175 | 1709.9757
|  | q @12 hrs | q @14 hrs | q @16 hrs
| TOTAL SENSIBLE COOLOING LOAD | 7085.4794 | 7463.5573 | 7993.9312
| TOTAL LATENT COOLOING LOAD | 2004.9757 | 2004.9757 | 2004.9757

## FIRST AID ROOM
FIRST-AID ROOM
| OVERALL HEAT TRANSFER COEFFICIENT (U) | LENGTH | WIDTH | HEIGHT | EFFECTIVE AREA | LM | SHGF | SC | CLTD/TD @12 | CLTD (CORR) @12 | CLF @12 | COOLING LOAD q @12 | CLTD/TD @14 | CLTD (CORR) @14 | CLF @14 | COOLING LOAD q @14 | CLTD/TD @16 | CLTD (CORR) @16 | CLF @16 | COOLING LOAD q @16
ROOF | 1.09 | 4.04 | 5.03 |  | 20.3212 | 1 |  |  | 12 | 32.1 |  | 711.0185 | 17 | 37.1 |  | 821.769 | 22 | 42.1 |  | 932.5195
EXPOSED WALL (EAST) | 0.9059 | 4.04 | 5.03 |  | 16.3588 | 0 |  |  | 15 | 34.1 |  | 505.3428 | 17.7778 | 36.8778 |  | 546.5079 | 18.3333 | 37.4333 |  | 554.7409
FLOOR | 1.09 | 4.04 | 5.03 |  | 20.3212 |  |  |  | 18 |  |  | 398.7019 | 18 |  |  | 398.7019 | 18 |  |  | 398.7019
PARTITION WALL (EAST) | 1.349 | 4.04 |  | 3.65 | 14.746 |  |  |  | 18 |  |  | 358.0624 | 18 |  |  | 358.0624 | 18 |  |  | 358.0624
PARTITION WALL (WEST)+DOOR | 1.5441 |  |  |  | 18.71 |  |  |  | 18 |  |  | 520.022 | 18 |  |  | 520.022 | 18 |  |  | 499.8
PARTITION WALL (SOUTH) | 1.349 |  | 5.03 | 3.65 | 18.3595 |  |  |  | 18 |  |  | 445.8054 | 18 |  |  | 445.8054 | 18 |  |  | 499.8
PARTITION WALL (NORTH) | 1.4964 |  | 5.03 | 3.65 | 19.36 |  |  |  | 18 |  |  | 521.4655 | 18 |  |  | 521.4655 | 18 |  |  | 499.8
GLASS WINDOWS (NORTH) | 4.8 | 1 | 1 |  | 1 |  | 141.615 | 0.6 | 18 |  | 0.89 | 162.0224 | 18 |  | 0.86 | 159.4733 | 18 |  | 0.75 | 150.1267
[10 empty] | TOTAL |  | 3622.4408 |  |  |  | 3771.8074 |  |  |  | 3893.5515
a=0.65 and b=C FROM Table-16
| QUANTITY | INPUT | AREA | L.H.G | S.H.G. | CLF @12 | COOLING LOAD @12 | CLF @14 | COOLING LOAD @14 | CLF @16 | COOLING LOAD @16
LIGHTS | 2 | 406.424 | 20.3212 |  |  | 0.86 | 349.5246 | 0.88 | 357.6531 | 0.89 | 361.7174
PEOPLE (S.H.) | 5 |  |  |  | 73 | 0.85 | 310.25 | 0.89 | 324.85 | 0.92 | 335.8
PEOPLE (L.H.) | 5 |  |  | 59 |  |  | 295 |  | 295 |  | 295
COMPUTER | 3 |  |  |  | 65 | 0.87 | 169.65 | 0.9 | 175.5 | 0.93 | 181.35
PRINTER | 3 |  |  |  | 550 | 0.87 | 1435.5 | 0.9 | 1485 | 0.93 | 1534.5
BLOOD PRESSURE METER | 2 |  |  |  | 29 | 0.87 | 50.46 | 0.9 | 52.2 | 0.93 | 53.94
BLOOD WARMER | 2 |  |  |  | 114 | 0.87 | 198.36 | 0.9 | 205.2 | 0.93 | 212.04
PULSE OXIMETER | 2 |  |  |  | 20 | 0.87 | 34.8 | 0.9 | 36 | 0.93 | 37.2
|  | TOTAL |  |  |  |  | 2548.5446 |  | 2636.4031 |  | 2716.5474
| LENGTH | WIDTH | HEIGHT` | VOLUME | L/S | TD | HUMIDITY DIFFERENCE | COOLING LOAD
VENTILATION AND INFILTRATION (SENSIBLE) | 4.04 | 5.03 | 3.65 | 74.1724 | 41.2069 | 23 |  | 1167.6381
VENTILATION AND INFILTRATION (LATENT) | 4.04 | 5.03 | 3.65 | 74.1724 | 41.2069 |  | 0.0175 | 2172.0145
|  | q @12 hrs | q @14 hrs | q @16 hrs
| TOTAL SENSIBLE COOLOING LOAD | 7338.6236 | 7575.8486 | 7777.737
| TOTAL LATENT COOLOING LOAD | 2467.0145 | 2467.0145 | 2467.0145

## CLERK ROOM
CLERK ROOM
| OVERALL HEAT TRANSFER COEFFICIENT (U) | LENGTH | WIDTH | HEIGHT | EFFECTIVE AREA | LM | SHGF | SC | CLTD/TD @12 | CLTD (CORR) @12 | CLF @12 | COOLING LOAD q @12 | CLTD/TD @14 | CLTD (CORR) @14 | CLF @14 | COOLING LOAD q @14 | CLTD/TD @16 | CLTD (CORR) @16 | CLF @16 | COOLING LOAD q @16
ROOF | 1.09 | 4.04 | 5.03 |  | 20.3212 | 1 |  |  | 12 | 32.1 |  | 711.0185 | 17 | 37.1 |  | 821.769 | 22 | 42.1 |  | 932.5195
EXPOSED WALL (EAST) | 0.9059 | 4.04 | 5.03 |  | 16.3588 | 0 |  |  | 15 | 34.1 |  | 505.3428 | 17.7778 | 36.8778 |  | 546.5079 | 18.3333 | 37.4333 |  | 554.7409
FLOOR | 1.09 | 4.04 | 5.03 |  | 20.3212 |  |  |  | 18 |  |  | 398.7019 | 18 |  |  | 398.7019 | 18 |  |  | 398.7019
PARTITION WALL (EAST) | 1.349 | 4.04 |  | 3.65 | 14.746 |  |  |  | 18 |  |  | 358.0624 | 18 |  |  | 358.0624 | 18 |  |  | 358.0624
PARTITION WALL (WEST)+DOOR | 1.5441 |  |  |  | 18.71 |  |  |  | 18 |  |  | 520.022 | 18 |  |  | 520.022 | 18 |  |  | 499.8
PARTITION WALL (NORTH) | 1.349 |  | 5.03 | 3.65 | 18.3595 |  |  |  | 18 |  |  | 445.8054 | 18 |  |  | 445.8054 | 18 |  |  | 499.8
PARTITION WALL (SOUTH) | 1.4964 |  | 5.03 | 3.65 | 19.36 |  |  |  | 18 |  |  | 521.4655 | 18 |  |  | 521.4655 | 18 |  |  | 499.8
GLASS WINDOWS (SOUTH) | 4.8 | 1 | 1 |  | 1 |  | 144.762 | 0.6 | 18 |  | 0.83 | 158.4915 | 18 |  | 0.68 | 145.4629 | 18 |  | 0.35 | 116.8
[10 empty] | TOTAL |  | 3618.9099 |  |  |  | 3757.797 |  |  |  | 3860.2248
a=0.65 and b=C FROM Table-16
| QUANTITY | INPUT | AREA | L.H.G | S.H.G. | CLF @12 | COOLING LOAD @12 | CLF @14 | COOLING LOAD @14 | CLF @16 | COOLING LOAD @16
LIGHTS | 2 | 406.424 | 20.3212 |  |  | 0.86 | 349.5246 | 0.88 | 357.6531 | 0.89 | 361.7174
PEOPLE (S.H.) | 10 |  |  |  | 73 | 0.85 | 620.5 | 0.89 | 649.7 | 0.92 | 671.6
PEOPLE (L.H.) | 10 |  |  | 59 |  |  | 590 |  | 590 |  | 590
|  | TOTAL |  |  |  |  | 970.0246 |  | 1007.3531 |  | 1033.3174
| LENGTH | WIDTH | HEIGHT` | VOLUME | L/S | TD | HUMIDITY DIFFERENCE | COOLING LOAD
VENTILATION AND INFILTRATION (SENSIBLE) | 4.04 | 5.03 | 3.65 | 74.1724 | 41.2069 | 23 |  | 1167.6381
VENTILATION AND INFILTRATION (LATENT) | 4.04 | 5.03 | 3.65 | 74.1724 | 41.2069 |  | 0.0175 | 2172.0145
|  | q @12 hrs | q @14 hrs | q @16 hrs
| TOTAL SENSIBLE COOLOING LOAD | 5756.5726 | 5932.7882 | 6061.1803
| TOTAL LATENT COOLOING LOAD | 2762.0145 | 2762.0145 | 2762.0145

## C-1
COUNSELOR OFFICE-1
| OVERALL HEAT TRANSFER COEFFICIENT (U) | LENGTH | WIDTH | HEIGHT | EFFECTIVE AREA | LM | SHGF | SC | CLTD/TD @12 | CLTD (CORR) @12 | CLF @12 | COOLING LOAD q @12 | CLTD/TD @14 | CLTD (CORR) @14 | CLF @14 | COOLING LOAD q @14 | CLTD/TD @16 | CLTD (CORR) @16 | CLF @16 | COOLING LOAD q @16
ROOF | 1.09 | 5.45 | 6.02 |  | 32.809 | 1 |  |  | 12 | 32.1 |  | 1147.9541 | 17 | 37.1 |  | 1326.7632 | 22 | 42.1 |  | 1505.5722
EXPOSED WALL (WEST) | 0.9059 | 5.45 |  | 3.65 | 19.8925 | 0 |  |  | 5 | 24.1 |  | 434.2968 | 6.1111 | 25.21 |  | 454.2997 | 10 | 29.1 |  | 524.3999
EXPOSED WALL (SOUTH) | 0.9059 |  | 6.02 | 3.65 | 19.2604 | -6 |  |  | 5 | 18.1 |  | 315.8087 | 8.8889 | 21.9889 |  | 383.6621 | 13.3333 | 26.4333 |  | 461.2087
FLOOR | 1.09 | 5.45 | 6.02 |  | 32.809 |  |  |  | 18 |  |  | 643.7126 | 18 |  |  | 643.7126 | 18 |  |  | 643.7126
PARTITION WALL (EAST) | 1.349 | 5.45 |  | 3.65 | 14.4725 |  |  |  | 18 |  |  | 351.4212 | 18 |  |  | 351.4212 | 18 |  |  | 351.4212
PARTITION WALL (NORTH)+DOOR | 1.4899 |  |  |  | 25.935 |  |  |  | 18 |  |  | 695.53 | 18 |  |  | 695.53 | 18 |  |  | 499.8
GLASS WINDOWS (SOUTH) | 4.8 | 1.37 | 1.98 |  | 2.7126 |  | 144.762 | 0.6 | 18 |  | 0.83 | 429.924 | 18 |  | 0.68 | 394.5827 | 18 |  | 0.35 | 316.8317
[10 empty] | TOTAL |  | 4018.6475 |  |  |  | 4249.9714 |  |  |  | 4302.9464
a=0.65 and b=C FROM Table-16 (OPERATIONAL HOURS 9 TO 19 (10 HRS))
| QUANTITY | INPUT | AREA | L.H.G | S.H.G. | CLF @12 | COOLING LOAD @12 | CLF @14 | COOLING LOAD @14 | CLF @16 | COOLING LOAD @16
LIGHTS | 4 | 1312.36 | 32.809 |  |  | 0.8 | 1049.888 | 0.82 | 1076.1352 | 0.84 | 1102.3824
PEOPLE (S.H.) | 3 |  |  |  | 73 | 0.77 | 168.63 | 0.83 | 181.77 | 0.87 | 190.53
PEOPLE (L.H.) | 3 |  |  | 59 |  |  | 177 |  | 177 |  | 177
COMPUTER | 1 |  |  |  | 65 | 0.81 | 52.65 | 0.85 | 55.25 | 0.89 | 57.85
PRINTER | 1 |  |  |  | 550 | 0.81 | 445.5 | 0.85 | 467.5 | 0.89 | 489.5
STRESS TREADMILL | 1 |  |  |  | 173 | 0.81 | 140.13 | 0.85 | 147.05 | 0.89 | 153.97
ECG/RESP | 1 |  |  |  | 50 | 0.81 | 40.5 | 0.85 | 42.5 | 0.89 | 44.5
|  | TOTAL |  |  |  |  | 1897.298 |  | 1970.2052 |  | 2038.7324
| LENGTH | WIDTH | HEIGHT` | VOLUME | L/S | TD | HUMIDITY DIFFERENCE | COOLING LOAD
VENTILATION AND INFILTRATION (SENSIBLE) | 5.45 | 6.02 | 3.65 | 119.7528 | 66.5294 | 23 |  | 1885.176
VENTILATION AND INFILTRATION (LATENT) | 5.45 | 6.02 | 3.65 | 119.7528 | 66.5294 |  | 0.0175 | 3506.7626
|  | q @12 hrs | q @14 hrs | q @16 hrs
| TOTAL SENSIBLE COOLOING LOAD | 7801.1215 | 8105.3526 | 8226.8548
| TOTAL LATENT COOLOING LOAD | 3683.7626 | 3683.7626 | 3683.7626

## C-2
COUNSELOR OFFICE-2
| OVERALL HEAT TRANSFER COEFFICIENT (U) | LENGTH | WIDTH | HEIGHT | EFFECTIVE AREA | LM | SHGF | SC | CLTD/TD @12 | CLTD (CORR) @12 | CLF @12 | COOLING LOAD q @12 | CLTD/TD @14 | CLTD (CORR) @14 | CLF @14 | COOLING LOAD q @14 | CLTD/TD @16 | CLTD (CORR) @16 | CLF @16 | COOLING LOAD q @16
ROOF | 1.09 | 5.45 | 6.02 |  | 32.809 | 1 |  |  | 12 | 32.1 |  | 1147.9541 | 17 | 37.1 |  | 1326.7632 | 22 | 42.1 |  | 1505.5722
EXPOSED WALL (SOUTH) | 0.9059 |  | 6.02 | 3.65 | 19.2604 | -6 |  |  | 5 | 18.1 |  | 315.8087 | 8.8889 | 21.9889 |  | 383.6621 | 13.3333 | 26.4333 |  | 461.2087
FLOOR | 1.09 | 5.45 | 6.02 |  | 32.809 |  |  |  | 18 |  |  | 643.7126 | 18 |  |  | 643.7126 | 18 |  |  | 643.7126
PARTITION WALL (EAST) | 1.349 | 5.45 |  | 3.65 | 14.4725 |  |  |  | 18 |  |  | 351.4212 | 18 |  |  | 351.4212 | 18 |  |  | 351.4212
PARTITION WALL (WEST) | 1.349 | 5.45 |  | 3.65 | 14.4725 |  |  |  | 18 |  |  | 351.4212 | 18 |  |  | 351.4212 | 18 |  |  | 351.4212
PARTITION WALL (NORTH)+DOOR | 1.4899 |  |  |  | 25.935 |  |  |  | 18 |  |  | 695.53 | 18 |  |  | 695.53 | 18 |  |  | 499.8
GLASS WINDOWS (SOUTH) | 4.8 | 1.37 | 1.98 |  | 2.7126 |  | 144.762 | 0.6 | 18 |  | 0.83 | 429.924 | 18 |  | 0.68 | 394.5827 | 18 |  | 0.35 | 316.8317
[10 empty] | TOTAL |  | 3935.7719 |  |  |  | 4147.0929 |  |  |  | 4129.9677
a=0.65 and b=C FROM Table-16 (OPERATIONAL HOURS 9 TO 19 (10 HRS))
| QUANTITY | INPUT | AREA | L.H.G | S.H.G. | CLF @12 | COOLING LOAD @12 | CLF @14 | COOLING LOAD @14 | CLF @16 | COOLING LOAD @16
LIGHTS | 4 | 1312.36 | 32.809 |  |  | 0.8 | 1049.888 | 0.82 | 1076.1352 | 0.84 | 1102.3824
PEOPLE (S.H.) | 3 |  |  |  | 73 | 0.77 | 168.63 | 0.83 | 181.77 | 0.87 | 190.53
PEOPLE (L.H.) | 3 |  |  | 59 |  |  | 177 |  | 177 |  | 177
COMPUTER | 1 |  |  |  | 65 | 0.81 | 52.65 | 0.85 | 55.25 | 0.89 | 57.85
PRINTER | 1 |  |  |  | 550 | 0.81 | 445.5 | 0.85 | 467.5 | 0.89 | 489.5
BLOOD PRESSURE METER | 1 |  |  |  | 29 | 0.81 | 23.49 | 0.85 | 24.65 | 0.89 | 25.81
ECG/RESP | 1 |  |  |  | 50 | 0.81 | 40.5 | 0.85 | 42.5 | 0.89 | 44.5
|  | TOTAL |  |  |  |  | 1780.658 |  | 1847.8052 |  | 1910.5724
| LENGTH | WIDTH | HEIGHT` | VOLUME | L/S | TD | HUMIDITY DIFFERENCE | COOLING LOAD
VENTILATION AND INFILTRATION (SENSIBLE) | 5.45 | 6.02 | 3.65 | 119.7528 | 66.5294 | 23 |  | 1885.176
VENTILATION AND INFILTRATION (LATENT) | 5.45 | 6.02 | 3.65 | 119.7528 | 66.5294 |  | 0.0175 | 3506.7626
|  | q @12 hrs | q @14 hrs | q @16 hrs
| TOTAL SENSIBLE COOLOING LOAD | 7601.6059 | 7880.0741 | 7925.7161
| TOTAL LATENT COOLOING LOAD | 3683.7626 | 3683.7626 | 3683.7626

## C-3
COUNSELOR OFFICE-3
| OVERALL HEAT TRANSFER COEFFICIENT (U) | LENGTH | WIDTH | HEIGHT | EFFECTIVE AREA | LM | SHGF | SC | CLTD/TD @12 | CLTD (CORR) @12 | CLF @12 | COOLING LOAD q @12 | CLTD/TD @14 | CLTD (CORR) @14 | CLF @14 | COOLING LOAD q @14 | CLTD/TD @16 | CLTD (CORR) @16 | CLF @16 | COOLING LOAD q @16
ROOF | 1.09 | 5.45 | 6.02 |  | 32.809 | 1 |  |  | 12 | 32.1 |  | 1147.9541 | 17 | 37.1 |  | 1326.7632 | 22 | 42.1 |  | 1505.5722
EXPOSED WALL (SOUTH) | 0.9059 |  | 6.02 | 3.65 | 19.2604 | -6 |  |  | 5 | 18.1 |  | 315.8087 | 8.8889 | 21.9889 |  | 383.6621 | 13.3333 | 26.4333 |  | 461.2087
FLOOR | 1.09 | 5.45 | 6.02 |  | 32.809 |  |  |  | 18 |  |  | 643.7126 | 18 |  |  | 643.7126 | 18 |  |  | 643.7126
PARTITION WALL (EAST) | 1.349 | 5.45 |  | 3.65 | 14.4725 |  |  |  | 18 |  |  | 351.4212 | 18 |  |  | 351.4212 | 18 |  |  | 351.4212
PARTITION WALL (WEST) | 1.349 | 5.45 |  | 3.65 | 14.4725 |  |  |  | 18 |  |  | 351.4212 | 18 |  |  | 351.4212 | 18 |  |  | 351.4212
PARTITION WALL (NORTH)+DOOR | 1.4899 |  |  |  | 25.935 |  |  |  | 18 |  |  | 695.53 | 18 |  |  | 695.53 | 18 |  |  | 499.8
GLASS WINDOWS (SOUTH) | 4.8 | 1.37 | 1.98 |  | 2.7126 |  | 144.762 | 0.6 | 18 |  | 0.83 | 429.924 | 18 |  | 0.68 | 394.5827 | 18 |  | 0.35 | 316.8317
[10 empty] | TOTAL |  | 3935.7719 |  |  |  | 4147.0929 |  |  |  | 4129.9677
a=0.65 and b=C FROM Table-16 (OPERATIONAL HOURS 9 TO 19 (10 HRS))
| QUANTITY | INPUT | AREA | L.H.G | S.H.G. | CLF @12 | COOLING LOAD @12 | CLF @14 | COOLING LOAD @14 | CLF @16 | COOLING LOAD @16
LIGHTS | 4 | 1312.36 | 32.809 |  |  | 0.8 | 1049.888 | 0.82 | 1076.1352 | 0.84 | 1102.3824
PEOPLE (S.H.) | 3 |  |  |  | 73 | 0.77 | 168.63 | 0.83 | 181.77 | 0.87 | 190.53
PEOPLE (L.H.) | 3 |  |  | 59 |  |  | 177 |  | 177 |  | 177
COMPUTER | 1 |  |  |  | 65 | 0.81 | 52.65 | 0.85 | 55.25 | 0.89 | 57.85
PRINTER | 1 |  |  |  | 550 | 0.81 | 445.5 | 0.85 | 467.5 | 0.89 | 489.5
BLOOD PRESSURE METER | 1 |  |  |  | 29 | 0.81 | 23.49 | 0.85 | 24.65 | 0.89 | 25.81
ECG/RESP | 1 |  |  |  | 50 | 0.81 | 40.5 | 0.85 | 42.5 | 0.89 | 44.5
|  | TOTAL |  |  |  |  | 1780.658 |  | 1847.8052 |  | 1910.5724
| LENGTH | WIDTH | HEIGHT` | VOLUME | L/S | TD | HUMIDITY DIFFERENCE | COOLING LOAD
VENTILATION AND INFILTRATION (SENSIBLE) | 5.45 | 6.02 | 3.65 | 119.7528 | 66.5294 | 23 |  | 1885.176
VENTILATION AND INFILTRATION (LATENT) | 5.45 | 6.02 | 3.65 | 119.7528 | 66.5294 |  | 0.0175 | 3506.7626
|  | q @12 hrs | q @14 hrs | q @16 hrs
| TOTAL SENSIBLE COOLOING LOAD | 7601.6059 | 7880.0741 | 7925.7161
| TOTAL LATENT COOLOING LOAD | 3683.7626 | 3683.7626 | 3683.7626

## C-4
COUNSELOR OFFICE-4
| OVERALL HEAT TRANSFER COEFFICIENT (U) | LENGTH | WIDTH | HEIGHT | EFFECTIVE AREA | LM | SHGF | SC | CLTD/TD @12 | CLTD (CORR) @12 | CLF @12 | COOLING LOAD q @12 | CLTD/TD @14 | CLTD (CORR) @14 | CLF @14 | COOLING LOAD q @14 | CLTD/TD @16 | CLTD (CORR) @16 | CLF @16 | COOLING LOAD q @16
ROOF | 1.09 | 5.45 | 6.02 |  | 32.809 | 1 |  |  | 12 | 32.1 |  | 1147.9541 | 17 | 37.1 |  | 1326.7632 | 22 | 42.1 |  | 1505.5722
EXPOSED WALL (SOUTH) | 0.9059 |  | 6.02 | 3.65 | 19.2604 | -6 |  |  | 5 | 18.1 |  | 315.8087 | 8.8889 | 21.9889 |  | 383.6621 | 13.3333 | 26.4333 |  | 461.2087
FLOOR | 1.09 | 5.45 | 6.02 |  | 32.809 |  |  |  | 18 |  |  | 643.7126 | 18 |  |  | 643.7126 | 18 |  |  | 643.7126
PARTITION WALL (EAST) | 1.349 | 5.45 |  | 3.65 | 14.4725 |  |  |  | 18 |  |  | 351.4212 | 18 |  |  | 351.4212 | 18 |  |  | 351.4212
PARTITION WALL (WEST) | 1.349 | 5.45 |  | 3.65 | 14.4725 |  |  |  | 18 |  |  | 351.4212 | 18 |  |  | 351.4212 | 18 |  |  | 351.4212
PARTITION WALL (NORTH)+DOOR | 1.4899 |  |  |  | 25.935 |  |  |  | 18 |  |  | 695.53 | 18 |  |  | 695.53 | 18 |  |  | 499.8
GLASS WINDOWS (SOUTH) | 4.8 | 1.37 | 1.98 |  | 2.7126 |  | 144.762 | 0.6 | 18 |  | 0.83 | 429.924 | 18 |  | 0.68 | 394.5827 | 18 |  | 0.35 | 316.8317
[9 empty] | TOTAL |  |  | 3935.7719 |  |  |  | 4147.0929 |  |  |  | 4129.9677
a=0.65 and b=C FROM Table-16 (OPERATIONAL HOURS 9 TO 19 (10 HRS))
| QUANTITY | INPUT | AREA | L.H.G | S.H.G. | CLF @12 | COOLING LOAD @12 | CLF @14 | COOLING LOAD @14 | CLF @16 | COOLING LOAD @16
LIGHTS | 4 | 1312.36 | 32.809 |  |  | 0.8 | 1049.888 | 0.82 | 1076.1352 | 0.84 | 1102.3824
PEOPLE (S.H.) | 3 |  |  |  | 73 | 0.77 | 168.63 | 0.83 | 181.77 | 0.87 | 190.53
PEOPLE (L.H.) | 3 |  |  | 59 |  |  | 177 |  | 177 |  | 177
COMPUTER | 1 |  |  |  | 65 | 0.81 | 52.65 | 0.85 | 55.25 | 0.89 | 57.85
PRINTER | 1 |  |  |  | 550 | 0.81 | 445.5 | 0.85 | 467.5 | 0.89 | 489.5
BLOOD PRESSURE METER | 1 |  |  |  | 29 | 0.81 | 23.49 | 0.85 | 24.65 | 0.89 | 25.81
ECG/RESP | 1 |  |  |  | 50 | 0.81 | 40.5 | 0.85 | 42.5 | 0.89 | 44.5
|  | TOTAL |  |  |  |  | 1780.658 |  | 1847.8052 |  | 1910.5724
| LENGTH | WIDTH | HEIGHT` | VOLUME | L/S | TD | HUMIDITY DIFFERENCE | COOLING LOAD
VENTILATION AND INFILTRATION (SENSIBLE) | 5.45 | 6.02 | 3.65 | 119.7528 | 66.5294 | 23 |  | 1885.176
VENTILATION AND INFILTRATION (LATENT) | 5.45 | 6.02 | 3.65 | 119.7528 | 66.5294 |  | 0.0175 | 3506.7626
|  | q @12 hrs | q @14 hrs | q @16 hrs
| TOTAL SENSIBLE COOLOING LOAD | 7601.6059 | 7880.0741 | 7925.7161
| TOTAL LATENT COOLOING LOAD | 3683.7626 | 3683.7626 | 3683.7626

## C-6
COUNSELOR OFFICE-6
| OVERALL HEAT TRANSFER COEFFICIENT (U) | LENGTH | WIDTH | HEIGHT | EFFECTIVE AREA | LM | SHGF | SC | CLTD/TD @12 | CLTD (CORR) @12 | CLF @12 | COOLING LOAD q @12 | CLTD/TD @14 | CLTD (CORR) @14 | CLF @14 | COOLING LOAD q @14 | CLTD/TD @16 | CLTD (CORR) @16 | CLF @16 | COOLING LOAD q @16
ROOF | 1.09 | 5.45 | 6.02 |  | 32.809 | 1 |  |  | 12 | 32.1 |  | 1147.9541 | 17 | 37.1 |  | 1326.7632 | 22 | 42.1 |  | 1505.5722
EXPOSED WALL (SOUTH) | 0.9059 |  | 6.02 | 3.65 | 19.2604 | -6 |  |  | 5 | 18.1 |  | 315.8087 | 8.8889 | 21.9889 |  | 383.6621 | 13.3333 | 26.4333 |  | 461.2087
FLOOR | 1.09 | 5.45 | 6.02 |  | 32.809 |  |  |  | 18 |  |  | 643.7126 | 18 |  |  | 643.7126 | 18 |  |  | 643.7126
PARTITION WALL (EAST) | 1.349 | 5.45 |  | 3.65 | 14.4725 |  |  |  | 18 |  |  | 351.4212 | 18 |  |  | 351.4212 | 18 |  |  | 351.4212
PARTITION WALL (WEST) | 1.349 | 5.45 |  | 3.65 | 14.4725 |  |  |  | 18 |  |  | 351.4212 | 18 |  |  | 351.4212 | 18 |  |  | 351.4212
PARTITION WALL (NORTH)+DOOR | 1.4899 |  |  |  | 25.935 |  |  |  | 18 |  |  | 695.53 | 18 |  |  | 695.53 | 18 |  |  | 499.8
GLASS WINDOWS (SOUTH) | 4.8 | 1.37 | 1.98 |  | 2.7126 |  | 144.762 | 0.6 | 18 |  | 0.83 | 429.924 | 18 |  | 0.68 | 394.5827 | 18 |  | 0.35 | 316.8317
[9 empty] | TOTAL |  |  | 3935.7719 |  |  |  | 4147.0929 |  |  |  | 4129.9677
a=0.65 and b=C FROM Table-16 (OPERATIONAL HOURS 9 TO 19 (10 HRS))
| QUANTITY | INPUT | AREA | L.H.G | S.H.G. | CLF @12 | COOLING LOAD @12 | CLF @14 | COOLING LOAD @14 | CLF @16 | COOLING LOAD @16
LIGHTS | 4 | 1312.36 | 32.809 |  |  | 0.8 | 1049.888 | 0.82 | 1076.1352 | 0.84 | 1102.3824
PEOPLE (S.H.) | 3 |  |  |  | 73 | 0.77 | 168.63 | 0.83 | 181.77 | 0.87 | 190.53
PEOPLE (L.H.) | 3 |  |  | 59 |  |  | 177 |  | 177 |  | 177
COMPUTER | 1 |  |  |  | 65 | 0.81 | 52.65 | 0.85 | 55.25 | 0.89 | 57.85
PRINTER | 1 |  |  |  | 550 | 0.81 | 445.5 | 0.85 | 467.5 | 0.89 | 489.5
BLOOD PRESSURE METER | 1 |  |  |  | 29 | 0.81 | 23.49 | 0.85 | 24.65 | 0.89 | 25.81
ECG/RESP | 1 |  |  |  | 50 | 0.81 | 40.5 | 0.85 | 42.5 | 0.89 | 44.5
|  | TOTAL |  |  |  |  | 1780.658 |  | 1847.8052 |  | 1910.5724
| LENGTH | WIDTH | HEIGHT` | VOLUME | L/S | TD | HUMIDITY DIFFERENCE | COOLING LOAD
VENTILATION AND INFILTRATION (SENSIBLE) | 5.45 | 6.02 | 3.65 | 119.7528 | 66.5294 | 23 |  | 1885.176
VENTILATION AND INFILTRATION (LATENT) | 5.45 | 6.02 | 3.65 | 119.7528 | 66.5294 |  | 0.0175 | 3506.7626
|  | q @12 hrs | q @14 hrs | q @16 hrs
| TOTAL SENSIBLE COOLOING LOAD | 7601.6059 | 7880.0741 | 7925.7161
| TOTAL LATENT COOLOING LOAD | 3683.7626 | 3683.7626 | 3683.7626

## C-7
COUNSELOR OFFICE-7
| OVERALL HEAT TRANSFER COEFFICIENT (U) | LENGTH | WIDTH | HEIGHT | EFFECTIVE AREA | LM | SHGF | SC | CLTD/TD @12 | CLTD (CORR) @12 | CLF @12 | COOLING LOAD q @12 | CLTD/TD @14 | CLTD (CORR) @14 | CLF @14 | COOLING LOAD q @14 | CLTD/TD @16 | CLTD (CORR) @16 | CLF @16 | COOLING LOAD q @16
ROOF | 1.09 | 5.45 | 6.02 |  | 32.809 | 1 |  |  | 12 | 32.1 |  | 1147.9541 | 17 | 37.1 |  | 1326.7632 | 22 | 42.1 |  | 1505.5722
EXPOSED WALL (EAST) | 0.9059 | 5.45 |  | 3.65 | 19.8925 | 0 |  |  | 15 | 34.1 |  | 614.503 | 17.7778 | 36.8778 |  | 664.5603 | 18.3333 | 37.4333 |  | 674.5717
EXPOSED WALL (SOUTH) | 0.9059 |  | 6.02 | 3.65 | 19.2604 | -6 |  |  | 5 | 18.1 |  | 315.8087 | 8.8889 | 21.9889 |  | 383.6621 | 13.3333 | 26.4333 |  | 461.2087
FLOOR | 1.09 | 5.45 | 6.02 |  | 32.809 |  |  |  | 18 |  |  | 643.7126 | 18 |  |  | 643.7126 | 18 |  |  | 643.7126
PARTITION WALL (WEST) | 1.349 | 5.45 |  | 3.65 | 14.4725 |  |  |  | 18 |  |  | 351.4212 | 18 |  |  | 351.4212 | 18 |  |  | 351.4212
PARTITION WALL (NORTH)+DOOR | 1.4899 |  |  |  | 25.935 |  |  |  | 18 |  |  | 695.53 | 18 |  |  | 695.53 | 18 |  |  | 499.8
GLASS WINDOWS (SOUTH) | 4.8 | 1.37 | 1.98 |  | 2.7126 |  | 144.762 | 0.6 | 18 |  | 0.83 | 859.848 | 18 |  | 0.68 | 394.5827 | 18 |  | 0.35 | 316.8317
[10 empty] | TOTAL |  | 4628.7776 |  |  |  | 4460.232 |  |  |  | 4453.1182
a=0.65 and b=C FROM Table-16 (OPERATIONAL HOURS 9 TO 19 (10 HRS))
| QUANTITY | INPUT | AREA | L.H.G | S.H.G. | CLF @12 | COOLING LOAD @12 | CLF @14 | COOLING LOAD @14 | CLF @16 | COOLING LOAD @16
LIGHTS | 4 | 1312.36 | 32.809 |  |  | 0.8 | 1049.888 | 0.82 | 1076.1352 | 0.84 | 1102.3824
PEOPLE (S.H.) | 3 |  |  |  | 73 | 0.77 | 168.63 | 0.83 | 181.77 | 0.87 | 190.53
PEOPLE (L.H.) | 3 |  |  | 59 |  |  | 177 |  | 177 |  | 177
COMPUTER | 1 |  |  |  | 65 | 0.81 | 52.65 | 0.85 | 55.25 | 0.89 | 57.85
PRINTER | 1 |  |  |  | 550 | 0.81 | 445.5 | 0.85 | 467.5 | 0.89 | 489.5
BLOOD PRESSURE METER | 1 |  |  |  | 29 | 0.81 | 23.49 | 0.85 | 24.65 | 0.89 | 25.81
ECG/RESP | 1 |  |  |  | 50 | 0.81 | 40.5 | 0.85 | 42.5 | 0.89 | 44.5
|  | TOTAL |  |  |  |  | 1780.658 |  | 1847.8052 |  | 1910.5724
| LENGTH | WIDTH | HEIGHT` | VOLUME | L/S | TD | HUMIDITY DIFFERENCE | COOLING LOAD
VENTILATION AND INFILTRATION (SENSIBLE) | 5.45 | 6.02 | 3.65 | 119.7528 | 66.5294 | 23 |  | 1885.176
VENTILATION AND INFILTRATION (LATENT) | 5.45 | 6.02 | 3.65 | 119.7528 | 66.5294 |  | 0.0175 | 3506.7626
|  | q @12 hrs | q @14 hrs | q @16 hrs
| TOTAL SENSIBLE COOLOING LOAD | 8294.6116 | 8193.2131 | 8248.8666
| TOTAL LATENT COOLOING LOAD | 3683.7626 | 3683.7626 | 3683.7626

## E-2
EXAMINATION ROOM-2
| OVERALL HEAT TRANSFER COEFFICIENT (U) | LENGTH | WIDTH | HEIGHT | EFFECTIVE AREA | LM | SHGF | SC | CLTD/TD @12 | CLTD (CORR) @12 | CLF @12 | COOLING LOAD q @12 | CLTD/TD @14 | CLTD (CORR) @14 | CLF @14 | COOLING LOAD q @14 | CLTD/TD @16 | CLTD (CORR) @16 | CLF @16 | COOLING LOAD q @16
ROOF | 1.09 | 4.5 | 8.077 |  | 36.3465 | 1 |  |  | 12 | 32.1 |  | 1271.7277 | 17 | 37.1 |  | 1469.8161 | 22 | 42.1 |  | 1667.9045
EXPOSED WALL (NORTH) | 0.9059 | 4.5 |  | 3.65 | 13.7124 | 1 |  |  | 3.8889 | 23.9889 |  | 297.9915 | 5.5556 | 25.6556 |  | 318.6949 | 7.2222 | 27.3222 |  | 339.3984
FLOOR | 1.09 | 4.5 | 8.077 |  | 36.3465 |  |  |  | 18 |  |  | 713.1183 | 18 |  |  | 713.1183 | 18 |  |  | 713.1183
PARTITION WALL (EAST) | 1.349 | 4.5 |  | 3.65 | 11.005 |  |  |  | 18 |  |  | 267.2234 | 18 |  |  | 267.2234 | 18 |  |  | 267.2234
PARTITION WALL (WEST) | 1.349 | 4.5 |  | 3.65 | 11.005 |  |  |  | 18 |  |  | 267.2234 | 18 |  |  | 267.2234 | 18 |  |  | 267.2234
PARTITION WALL (SOUTH)+DOOR | 0.9318 |  |  |  | 29.481 |  |  |  | 18 |  |  | 494.468 | 18 |  |  | 494.468 | 18 |  |  | 499.8
GLASS WINDOWS (NORTH) | 4.8 | 1.37 | 1.98 |  | 2.7126 |  | 141.615 | 0.6 | 18 |  | 0.89 | 439.502 | 18 |  | 0.86 | 432.5874 | 18 |  | 0.75 | 407.2338
[10 empty] | TOTAL |  | 3751.2543 |  |  |  | 3963.1315 |  |  |  | 4161.9019
a=0.65 and b=C FROM Table-16
| QUANTITY | INPUT | AREA | L.H.G | S.H.G. | CLF @12 | COOLING LOAD @12 | CLF @14 | COOLING LOAD @14 | CLF @16 | COOLING LOAD @16
LIGHTS | 4 | 1453.86 | 36.3465 |  |  | 0.86 | 1250.3196 | 0.88 | 1279.3968 | 0.89 | 1293.9354
PEOPLE (S.H.) | 2 |  |  |  | 73 | 0.82 | 119.72 | 0.87 | 127.02 | 0.9 | 131.4
PEOPLE (L.H.) | 2 |  |  | 59 |  |  | 118 |  | 118 |  | 118
BLANKET WARMER | 1 |  |  |  | 221 | 0.85 | 187.85 | 0.87 | 192.27 | 0.9 | 198.9
BLOOD WARMER | 1 |  |  |  | 114 | 0.85 | 96.9 | 0.87 | 99.18 | 0.9 | 102.6
BLOOOD PRESSURE METER | 1 |  |  |  | 29 | 0.23 | 6.67 | 0.14 | 4.06 | 0.1 | 2.9
ECG/RESP | 1 |  |  |  | 50 | 0.23 | 11.5 | 0.14 | 7 | 0.1 | 5
PULSE OXIMETER | 1 |  |  |  | 20 | 0.23 | 4.6 | 0.14 | 2.8 | 0.1 | 2
ANESTHESIA SYSTEM | 1 |  |  |  | 166 | 0.23 | 38.18 | 0.14 | 23.24 | 0.1 | 16.6
|  | TOTAL |  |  |  |  | 1715.7396 |  | 1734.9668 |  | 1753.3354
| LENGTH | WIDTH | HEIGHT` | VOLUME | L/S | TD | HUMIDITY DIFFERENCE | COOLING LOAD
VENTILATION AND INFILTRATION (SENSIBLE) | 4.5 | 8.077 | 3.65 | 132.6647 | 73.7026 | 23 |  | 2088.4376
VENTILATION AND INFILTRATION (LATENT) | 4.5 | 8.077 | 3.65 | 132.6647 | 73.7026 |  | 0.0175 | 3884.8654
|  | q @12 hrs | q @14 hrs | q @16 hrs
| TOTAL SENSIBLE COOLOING LOAD | 7555.4315 | 7786.5359 | 8003.6749
| TOTAL LATENT COOLOING LOAD | 4002.8654 | 4002.8654 | 4002.8654

## E-3
EXAMINATION ROOM-3
| OVERALL HEAT TRANSFER COEFFICIENT (U) | LENGTH | WIDTH | HEIGHT | EFFECTIVE AREA | LM | SHGF | SC | CLTD/TD @12 | CLTD (CORR) @12 | CLF @12 | COOLING LOAD q @12 | CLTD/TD @14 | CLTD (CORR) @14 | CLF @14 | COOLING LOAD q @14 | CLTD/TD @16 | CLTD (CORR) @16 | CLF @16 | COOLING LOAD q @16
ROOF | 1.09 | 4.5 | 8.077 |  | 36.3465 | 1 |  |  | 12 | 32.1 |  | 1271.7277 | 17 | 37.1 |  | 1469.8161 | 22 | 42.1 |  | 1667.9045
EXPOSED WALL (NORTH) | 0.9059 | 4.5 |  | 3.65 | 13.7124 | 1 |  |  | 3.8889 | 23.9889 |  | 297.9915 | 5.5556 | 25.6556 |  | 318.6949 | 7.2222 | 27.3222 |  | 339.3984
FLOOR | 1.09 | 4.5 | 8.077 |  | 36.3465 |  |  |  | 18 |  |  | 713.1183 | 18 |  |  | 713.1183 | 18 |  |  | 713.1183
PARTITION WALL (EAST) | 1.349 | 4.5 |  | 3.65 | 11.005 |  |  |  | 18 |  |  | 267.2234 | 18 |  |  | 267.2234 | 18 |  |  | 267.2234
PARTITION WALL (WEST) | 1.349 | 4.5 |  | 3.65 | 11.005 |  |  |  | 18 |  |  | 267.2234 | 18 |  |  | 267.2234 | 18 |  |  | 267.2234
PARTITION WALL (SOUTH)+DOOR | 0.9318 |  |  |  | 29.481 |  |  |  | 18 |  |  | 494.468 | 18 |  |  | 494.468 | 18 |  |  | 499.8
GLASS WINDOWS (NORTH) | 4.8 | 1.37 | 1.98 |  | 2.7126 |  | 141.615 | 0.6 | 18 |  | 0.89 | 439.502 | 18 |  | 0.86 | 432.5874 | 18 |  | 0.75 | 407.2338
[10 empty] | TOTAL |  | 3751.2543 |  |  |  | 3963.1315 |  |  |  | 4161.9019
a=0.65 and b=C FROM Table-16
| QUANTITY | INPUT | AREA | L.H.G | S.H.G. | CLF @12 | COOLING LOAD @12 | CLF @14 | COOLING LOAD @14 | CLF @16 | COOLING LOAD @16
LIGHTS | 4 | 1453.86 | 36.3465 |  |  | 0.86 | 1250.3196 | 0.88 | 1279.3968 | 0.89 | 1293.9354
PEOPLE (S.H.) | 2 |  |  |  | 73 | 0.82 | 119.72 | 0.87 | 127.02 | 0.9 | 131.4
PEOPLE (L.H.) | 2 |  |  | 59 |  |  | 118 |  | 118 |  | 118
BLANKET WARMER | 1 |  |  |  | 221 | 0.85 | 187.85 | 0.87 | 192.27 | 0.9 | 198.9
BLOOD WARMER | 1 |  |  |  | 114 | 0.85 | 96.9 | 0.87 | 99.18 | 0.9 | 102.6
BLOOOD PRESSURE METER | 1 |  |  |  | 29 | 0.23 | 6.67 | 0.14 | 4.06 | 0.1 | 2.9
ECG/RESP | 1 |  |  |  | 50 | 0.23 | 11.5 | 0.14 | 7 | 0.1 | 5
PULSE OXIMETER | 1 |  |  |  | 20 | 0.23 | 4.6 | 0.14 | 2.8 | 0.1 | 2
ANESTHESIA SYSTEM | 1 |  |  |  | 166 | 0.23 | 38.18 | 0.14 | 23.24 | 0.1 | 16.6
|  | TOTAL |  |  |  |  | 1715.7396 |  | 1734.9668 |  | 1753.3354
| LENGTH | WIDTH | HEIGHT` | VOLUME | L/S | TD | HUMIDITY DIFFERENCE | COOLING LOAD
VENTILATION AND INFILTRATION (SENSIBLE) | 4.5 | 8.077 | 3.65 | 132.6647 | 73.7026 | 23 |  | 2088.4376
VENTILATION AND INFILTRATION (LATENT) | 4.5 | 8.077 | 3.65 | 132.6647 | 73.7026 |  | 0.0175 | 3884.8654
|  | q @12 hrs | q @14 hrs | q @16 hrs
| TOTAL SENSIBLE COOLOING LOAD | 7555.4315 | 7786.5359 | 8003.6749
| TOTAL LATENT COOLOING LOAD | 4002.8654 | 4002.8654 | 4002.8654

## E-4
EXAMINATION ROOM-4
| OVERALL HEAT TRANSFER COEFFICIENT (U) | LENGTH | WIDTH | HEIGHT | EFFECTIVE AREA | LM | SHGF | SC | CLTD/TD @12 | CLTD (CORR) @12 | CLF @12 | COOLING LOAD q @12 | CLTD/TD @14 | CLTD (CORR) @14 | CLF @14 | COOLING LOAD q @14 | CLTD/TD @16 | CLTD (CORR) @16 | CLF @16 | COOLING LOAD q @16
ROOF | 1.09 | 4.5 | 8.077 |  | 36.3465 | 1 |  |  | 12 | 32.1 |  | 1271.7277 | 17 | 37.1 |  | 1469.8161 | 22 | 42.1 |  | 1667.9045
EXPOSED WALL (NORTH) | 0.9059 | 4.5 |  | 3.65 | 13.7124 | 1 |  |  | 3.8889 | 23.9889 |  | 297.9915 | 5.5556 | 25.6556 |  | 318.6949 | 7.2222 | 27.3222 |  | 339.3984
FLOOR | 1.09 | 4.5 | 8.077 |  | 36.3465 |  |  |  | 18 |  |  | 713.1183 | 18 |  |  | 713.1183 | 18 |  |  | 713.1183
PARTITION WALL (EAST) | 1.349 | 4.5 |  | 3.65 | 11.005 |  |  |  | 18 |  |  | 267.2234 | 18 |  |  | 267.2234 | 18 |  |  | 267.2234
PARTITION WALL (WEST) | 1.349 | 4.5 |  | 3.65 | 11.005 |  |  |  | 18 |  |  | 267.2234 | 18 |  |  | 267.2234 | 18 |  |  | 267.2234
PARTITION WALL (SOUTH)+DOOR | 0.9318 |  |  |  | 29.481 |  |  |  | 18 |  |  | 494.468 | 18 |  |  | 494.468 | 18 |  |  | 499.8
GLASS WINDOWS (NORTH) | 4.8 | 1.37 | 1.98 |  | 2.7126 |  | 141.615 | 0.6 | 18 |  | 0.89 | 439.502 | 18 |  | 0.86 | 432.5874 | 18 |  | 0.75 | 407.2338
[10 empty] | TOTAL |  | 3751.2543 |  |  |  | 3963.1315 |  |  |  | 4161.9019
a=0.65 and b=C FROM Table-16
| QUANTITY | INPUT | AREA | L.H.G | S.H.G. | CLF @12 | COOLING LOAD @12 | CLF @14 | COOLING LOAD @14 | CLF @16 | COOLING LOAD @16
LIGHTS | 4 | 1453.86 | 36.3465 |  |  | 0.86 | 1250.3196 | 0.88 | 1279.3968 | 0.89 | 1293.9354
PEOPLE (S.H.) | 4 |  |  |  | 73 | 0.82 | 239.44 | 0.87 | 254.04 | 0.9 | 262.8
PEOPLE (L.H.) | 4 |  |  | 59 |  |  | 236 |  | 236 |  | 236
BLANKET WARMER | 1 |  |  |  | 221 | 0.85 | 187.85 | 0.87 | 192.27 | 0.9 | 198.9
BLOOD WARMER | 1 |  |  |  | 114 | 0.85 | 96.9 | 0.87 | 99.18 | 0.9 | 102.6
BLOOOD PRESSURE METER | 1 |  |  |  | 29 | 0.23 | 6.67 | 0.14 | 4.06 | 0.1 | 2.9
ECG/RESP | 1 |  |  |  | 50 | 0.23 | 11.5 | 0.14 | 7 | 0.1 | 5
PULSE OXIMETER | 1 |  |  |  | 20 | 0.23 | 4.6 | 0.14 | 2.8 | 0.1 | 2
|  | TOTAL |  |  |  |  | 1797.2796 |  | 1838.7468 |  | 1868.1354
| LENGTH | WIDTH | HEIGHT` | VOLUME | L/S | TD | HUMIDITY DIFFERENCE | COOLING LOAD | `
VENTILATION AND INFILTRATION (SENSIBLE) | 4.5 | 8.077 | 3.65 | 132.6647 | 73.7026 | 23 |  | 2088.4376
VENTILATION AND INFILTRATION (LATENT) | 4.5 | 8.077 | 3.65 | 132.6647 | 73.7026 |  | 0.0175 | 3884.8654
|  | q @12 hrs | q @14 hrs | q @16 hrs
| TOTAL SENSIBLE COOLOING LOAD | 7636.9715 | 7890.3159 | 8118.4749
| TOTAL LATENT COOLOING LOAD | 4120.8654 | 4120.8654 | 4120.8654

## E-5
EXAMKINATION ROOM-5
| OVERALL HEAT TRANSFER COEFFICIENT (U) | LENGTH | WIDTH | HEIGHT | EFFECTIVE AREA | LM | SHGF | SC | CLTD/TD @12 | CLTD (CORR) @12 | CLF @12 | COOLING LOAD q @12 | CLTD/TD @14 | CLTD (CORR) @14 | CLF @14 | COOLING LOAD q @14 | CLTD/TD @16 | CLTD (CORR) @16 | CLF @16 | COOLING LOAD q @16
ROOF | 1.09 | 4.5 | 8.077 |  | 36.3465 | 1 |  |  | 12 | 32.1 |  | 1271.7277 | 17 | 37.1 |  | 1469.8161 | 22 | 42.1 |  | 1667.9045
EXPOSED WALL (EAST) | 0.9059 | 4.5 |  | 3.65 | 16.425 | 0 |  |  | 15 | 34.1 |  | 507.3878 | 17.7778 | 36.8778 |  | 548.7195 | 18.3333 | 37.4333 |  | 556.9858
EXPOSED WALL (SOUTH) | 0.9059 |  | 8.077 | 3.65 | 26.7685 | -6 |  |  | 5 | 18.1 |  | 438.9167 | 8.8889 | 21.9889 |  | 533.2204 | 13.3333 | 26.4333 |  | 640.9961
FLOOR | 1.09 | 4.5 | 8.077 |  | 36.3465 |  |  |  | 18 |  |  | 713.1183 | 18 |  |  | 713.1183 | 18 |  |  | 713.1183
PARTITION WALL (WEST) | 1.349 | 4.5 |  | 3.65 | 11.005 |  |  |  | 18 |  |  | 267.2234 | 18 |  |  | 267.2234 | 18 |  |  | 267.2234
PARTITION WALL (SOUTH)+DOOR | 0.9318 |  |  |  | 29.481 |  |  |  | 18 |  |  | 494.468 | 18 |  |  | 494.468 | 18 |  |  | 499.8
GLASS WINDOWS (SOUTH) | 4.8 | 1.37 | 1.98 |  | 2.7126 |  | 141.615 | 0.6 | 18 |  | 0.89 | 439.502 | 18 |  | 0.86 | 432.5874 | 18 |  | 0.75 | 407.2338
[10 empty] | TOTAL |  | 4132.3438 |  |  |  | 4459.1531 |  |  |  | 4753.2621
a=0.65 and b=C FROM Table-16 (OPERATIONAL HOURS 9 TO 19 (10 HRS))
| QUANTITY | INPUT | AREA | L.H.G | S.H.G. | CLF @12 | COOLING LOAD @12 | CLF @14 | COOLING LOAD @14 | CLF @16 | COOLING LOAD @16
LIGHTS | 4 | 1453.86 | 36.3465 |  |  | 0.8 | 1163.088 | 0.82 | 1192.1652 | 0.84 | 1221.2424
PEOPLE (S.H.) | 3 |  |  |  | 73 | 0.77 | 168.63 | 0.83 | 181.77 | 0.87 | 190.53
PEOPLE (L.H.) | 3 |  |  | 59 |  |  | 177 |  | 177 |  | 177
COMPUTER | 1 |  |  |  | 65 | 0.81 | 52.65 | 0.85 | 55.25 | 0.89 | 57.85
PRINTER | 1 |  |  |  | 550 | 0.81 | 445.5 | 0.85 | 467.5 | 0.89 | 489.5
BLOOD PRESSURE METER | 1 |  |  |  | 29 | 0.81 | 23.49 | 0.85 | 24.65 | 0.89 | 25.81
ECG/RESP | 1 |  |  |  | 50 | 0.81 | 40.5 | 0.85 | 42.5 | 0.89 | 44.5
|  | TOTAL |  |  |  |  | 1893.858 |  | 1963.8352 |  | 2029.4324
| LENGTH | WIDTH | HEIGHT` | VOLUME | L/S | TD | HUMIDITY DIFFERENCE | COOLING LOAD
VENTILATION AND INFILTRATION (SENSIBLE) | 4.5 | 8.077 | 3.65 | 132.6647 | 73.7026 | 23 |  | 2088.4376
VENTILATION AND INFILTRATION (LATENT) | 4.5 | 8.077 | 3.65 | 132.6647 | 73.7026 |  | 0.0175 | 3884.8654
|  | q @12 hrs | q @14 hrs | q @16 hrs
| TOTAL SENSIBLE COOLOING LOAD | 8114.6394 | 8511.4259 | 8871.132
| TOTAL LATENT COOLOING LOAD | 4061.8654 | 4061.8654 | 4061.8654

## STORAGE
STORAGE
| OVERALL HEAT TRANSFER COEFFICIENT (U) | LENGTH | WIDTH | HEIGHT | EFFECTIVE AREA | LM | SHGF | SC | CLTD/TD @12 | CLTD (CORR) @12 | CLF @12 | COOLING LOAD q @12 | CLTD/TD @14 | CLTD (CORR) @14 | CLF @14 | COOLING LOAD q @14 | CLTD/TD @16 | CLTD (CORR) @16 | CLF @16 | COOLING LOAD q @16
ROOF | 1.09 | 5.45 | 4.27 |  | 23.2715 | 1 |  |  | 12 | 32.1 |  | 814.2465 | 17 | 37.1 |  | 941.0762 | 22 | 42.1 |  | 1067.9059
EXPOSED WALL (SOUTH) | 0.9059 |  | 4.27 | 3.65 | 12.8729 | -6 |  |  | 5 | 18.1 |  | 211.0742 | 8.8889 | 21.9889 |  | 256.4247 | 13.3333 | 26.4333 |  | 308.2539
FLOOR | 1.09 | 5.45 | 6.02 |  | 32.809 |  |  |  | 18 |  |  | 643.7126 | 18 |  |  | 643.7126 | 18 |  |  | 643.7126
PARTITION WALL (EAST) | 1.349 | 5.45 |  | 3.65 | 14.4725 |  |  |  | 18 |  |  | 351.4212 | 18 |  |  | 351.4212 | 18 |  |  | 351.4212
PARTITION WALL (WEST) | 1.349 | 5.45 |  | 3.65 | 14.4725 |  |  |  | 18 |  |  | 351.4212 | 18 |  |  | 351.4212 | 18 |  |  | 351.4212
PARTITION WALL (NORTH)+DOOR | 1.4899 |  |  |  | 25.935 |  |  |  | 18 |  |  | 695.53 | 18 |  |  | 695.53 | 18 |  |  | 499.8
GLASS WINDOWS (SOUTH) | 4.8 | 1.37 | 1.98 |  | 2.7126 |  | 144.762 | 0.6 | 18 |  | 0.83 | 429.924 | 18 |  | 0.68 | 394.5827 | 18 |  | 0.35 | 316.8317
[10 empty] | TOTAL |  | 3497.3298 |  |  |  | 3634.1687 |  |  |  | 3539.3466
a=0.65 and b=C FROM Table-16 (OPERATIONAL HOURS 9 TO 19 (10 HRS))
| QUANTITY | INPUT | AREA | L.H.G | S.H.G. | CLF @12 | COOLING LOAD @12 | CLF @14 | COOLING LOAD @14 | CLF @16 | COOLING LOAD @16
LIGHTS | 4 | 930.86 | 23.2715 |  |  | 0.8 | 744.688 | 0.82 | 763.3052 | 0.84 | 781.9224
PEOPLE (S.H.) | 1 |  |  |  | 73 | 0.77 | 56.21 | 0.83 | 60.59 | 0.87 | 63.51
PEOPLE (L.H.) | 1 |  |  | 59 |  |  | 59 |  | 59 |  | 59
COMPUTER | 1 |  |  |  | 65 | 0.81 | 52.65 | 0.85 | 55.25 | 0.89 | 57.85
PRINTER | 1 |  |  |  | 550 | 0.81 | 445.5 | 0.85 | 467.5 | 0.89 | 489.5
|  | TOTAL |  |  |  |  | 1299.048 |  | 1346.6452 |  | 1392.7824
| LENGTH | WIDTH | HEIGHT` | VOLUME | L/S | TD | HUMIDITY DIFFERENCE | COOLING LOAD
VENTILATION AND INFILTRATION (SENSIBLE) | 5.45 | 4.27 | 3.65 | 84.941 | 47.1894 | 23 |  | 1337.1597
VENTILATION AND INFILTRATION (LATENT) | 5.45 | 4.27 | 3.65 | 84.941 | 47.1894 |  | 0.0175 | 2487.3549
|  | q @12 hrs | q @14 hrs | q @16 hrs
| TOTAL SENSIBLE COOLOING LOAD | 6133.5375 | 6317.9736 | 6269.2887
| TOTAL LATENT COOLOING LOAD | 2546.3549 | 2546.3549 | 2546.3549